## Sheet1
Concept / Method | Formula | Purpose / Meaning
Total Dissolved Combustible Gas (TDCG) | TDCG = H_2 + CH_4 + C_2H_6 + C_2H_4 + C_2H_2 + CO | Overall transformer health indicator
Gas Percentage Normalization | %Gas = \frac{Gas}{Total\ Gas}\times100 | Converts gas ppm into percentage
Duval Triangle Constraint | CH_4 + C_2H_4 + C_2H_2 = 100 | Ternary gas relationship
Rogers Ratio R₁ | R_1 = \frac{C_2H_2}{C_2H_4} | Detects discharge/arcing
Rogers Ratio R₂ | R_2 = \frac{CH_4}{H_2} | PD vs thermal fault
Rogers Ratio R₅ | R_5 = \frac{C_2H_4}{C_2H_6} | Thermal severity
Doernenburg Ratio 1 | \frac{CH_4}{H_2} | Thermal vs PD
Doernenburg Ratio 2 | \frac{C_2H_2}{C_2H_4} | Arcing detection
Doernenburg Ratio 3 | \frac{C_2H_2}{CH_4} | Discharge severity
IEC 60599 Ratio | \frac{CH_4}{H_2} | Thermal/PD classification
IEC 60599 Ratio | \frac{C_2H_2}{C_2H_4} | Electrical discharge classification
CO₂/CO Ratio | \frac{CO_2}{CO} | Paper insulation health
ppm Definition | ppm = \frac{Gas\ Molecules}{10^6\ Molecules} | Gas concentration measurement
Thermal Fault T1 | T1:<300^\circ C | Low-temperature overheating
Thermal Fault T2 | T2:300^\circ C-700^\circ C | Medium thermal fault
Thermal Fault T3 | T3:>700^\circ C | Severe overheating
Partial Discharge (PD) | PD \rightarrow H_2 | Low-energy dielectric discharge
Arcing Fault | Arcing \rightarrow C_2H_2 | High-energy electrical discharge
Low Thermal Fault | Low\ Thermal \rightarrow CH_4 | Mild oil overheating
High Thermal Fault | High\ Thermal \rightarrow C_2H_4 | Severe oil overheating
Cellulose Degradation | Paper\ Aging \rightarrow CO + CO_2 | Insulation deterioration
Transformer Power Relation | V_p I_p \approx V_s I_s | Transformer power transfer
Cartesian Conversion (Duval geometry) | x = 0.5(2b+c) | Ternary-to-graph conversion
Cartesian Conversion (Duval geometry) | y = \frac{\sqrt{3}}{2}c | Ternary plotting coordinate

## Sheet2
Method / Concept | What It Does
TDCG | Calculates total combustible gases to estimate overall transformer health
Gas Percentage Normalization | Converts raw ppm values into percentages for Duval analysis
Duval Triangle | Identifies transformer fault zone using CH₄, C₂H₄, and C₂H₂ percentages
Rogers Ratio Method | Diagnoses PD, thermal faults, and arcing using gas ratios
Doernenburg Ratio Method | Performs fault classification only when gas levels are sufficiently high
IEC 60599 Method | Uses international ratio standards for transformer fault diagnosis
Key Gas Method | Identifies dominant fault based on highest gas concentration
CO₂/CO Ratio | Evaluates paper/cellulose insulation degradation
ppm Measurement | Measures concentration of dissolved gases in oil
H₂ Analysis | Detects partial discharge or corona
CH₄ Analysis | Detects low-temperature overheating
C₂H₆ Analysis | Indicates moderate thermal decomposition
C₂H₄ Analysis | Indicates high-temperature overheating
C₂H₂ Analysis | Detects electrical arcing/high-energy discharge
CO Analysis | Detects paper insulation overheating
CO₂ Analysis | Detects insulation aging
Thermal Fault T1 | Indicates overheating below 300°C
Thermal Fault T2 | Indicates overheating between 300–700°C
Thermal Fault T3 | Indicates overheating above 700°C
Partial Discharge (PD) | Detects localized insulation ionization
Arcing Fault | Detects severe electrical discharge
Ternary Coordinate System | Converts three gas percentages into a point inside Duval triangle
Cartesian Conversion | Converts ternary percentages into x-y coordinates for plotting
Low-Gas Validation | Prevents false Duval fault classification at tiny gas concentrations
Threshold Logic | Compares gas values against standard engineering limits
Gas Limit Checking | Verifies whether gas concentrations exceed IEEE/IEC thresholds
Condition Monitoring | Tracks transformer health over time
Predictive Maintenance | Detects faults before catastrophic transformer failure
Transformer Diagnostics | Identifies type and severity of internal transformer faults
Fault Classification | Categorizes faults into thermal, discharge, arcing, PD, etc.
Insulation Health Analysis | Evaluates aging and degradation of transformer insulation
Utility Asset Monitoring | Helps utilities decide maintenance and operation strategy