## Transformer Oil Data
CSS Name | Transformer No. | Report Date | Sampling Date | Manufacturer | Rating (KVA) | Voltage Class (KV) | Type of Oil | BDV (KV) | Water Content (ppm) | Color (ASTM) | Density g/cm3 | Sp.Res 27C (x10^12 Ohm-cm) | Sp.Res 90C (x10^12 Ohm-cm) | DDF 27C (tand) | DDF 90C (tand) | IFT N/m | Neutralization mgKOH/g | Sediment % | Flash Point C | OQI | H2 ppm | O2 ppm | N2 ppm | CO ppm | CH4 ppm | CO2 ppm | C2H4 ppm | C2H6 ppm | C2H2 ppm | C3H6 ppm | C3H8 ppm | TDCG mg/kg | TGC v/v% | Overall Recommendation | Source PDF
AALAKANDA Humidity: 46% | V9325/2 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | CG Near Hotel Leela, Sahar Airport Road, $ | 11kV/433V $ | 1000kVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | ND | ND |  | ND | 26.40 | ND | 0.0065 | 0.0640 | ND | ND | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are not in the limits of Good criteria except Tan Delta test. $ ¦ Recommended to recondition the oil. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | AALAKANDA--TO24-002257.014-270324.pdf
ACHARYA VIDYOG Humidity: 47% | 1262 Andheri east, Mumbai 400059. | 28/03/2024 | 13/03/2024 | EMCO Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 51 | 29 |  | ND | 2447.50 | 229.2 | 0.0007 | 0.0060 | 36 | 0.0103 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | ACHARYA VIDYOG--TO24-002281.007-280324.pdf
Akash Ganga Humidity: 46% | 12250 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | ETE Near Hotel Leela, Sahar Airport Road, $ | 1000kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | ND | ND |  | ND | 18.42 | ND | 0.0090 | 0.0899 | ND | ND | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are not in the limits of Good criteria except Tan Delta test. $ ¦ Recommended to recondition the oil. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | Akash Ganga-TO24-002035.007-080324.pdf
Akash Ratnadeep Humidity: 46% | 4444/63 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | BBL Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | ND | ND |  | ND | 7130.00 | 619 | 0.0009 | 0.0090 | 32 | 0.0159 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are not in the limits of Good criteria except Acidity, IFT and Tan Delta test. $ ¦ Recommended to recondition the oil. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | Akash RatnadeepTR-1TO24-002035.008-080324.pdf
Akash Ratnadeep Humidity: 46% | 4444/23 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | BBL Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 67 | 13 |  | ND | 1001.60 | 904.2 | 0.0008 | 0.0084 | 36 | 0.0116 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | Akash RatnadeepTR-2TO24-002035.009-080324.pdf
AMAN ENTERPRISES Humidity: 45% | 554 Andheri east, Mumbai 400059. | 11/03/2024 | 08/03/2024 | EMCO Near Hotel Leela, Sahar Airport Road, $ | 750kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 65 | 15 |  | ND | 201.40 | 19.14 | 0.0015 | 0.0139 | 26 | 0.0365 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | AMAN ENTERPRISES-TO24-002116.005-110324.pdf
APPK Humidity: 45% | 1043 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | EMCO Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 52 | 28 |  | ND | 129.60 | 12.23 | 0.0015 | 0.0164 | ND | 0.0813 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria except IFT test. $ ¦ Recommended frequency of testing is once in a year. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | APPK TR-1TO24-002037.015-110324.pdf
APPK Humidity: 45% | 1255 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | EMCO Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 61 | 23 |  | ND | 3169.00 | 292.3 | 0.0010 | 0.0101 | 31 | 0.0180 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | APPK TR-2TO24-002037.013-110324.pdf
AVLON CSS Humidity: 45% | 01PMF60/17 Andheri east, Mumbai 400059. | 11/03/2024 | 08/03/2024 | KIRLOSKAR Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 64 | 16 |  | ND | 1844.60 | ND | 0.0008 | ND | ND | ND | 1866 | 1448 |  | ND | ND | ND | ND | ND | ND | ND | ND | ND |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | AVLON CSS-TO24-002116.001-110324.pdf
AVLON CSS Humidity: 45% | 01PMF60/17 Andheri east, Mumbai 400059. | 11/03/2024 | 08/03/2024 | KIRLOSKAR Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 72 | 7 |  | ND | 1349.10 | 108.4 | 0.0010 | 0.0096 | 36 | 0.0102 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | AVLON CSS-TO24-002116.002-110324.pdf
BRC 4D Humidity: 46% | 05PMD019/17 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | KIRLOSKAR Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 68 | 13 |  | ND | 26345.00 | 2376 | 0.0003 | 0.0017 | 36 | 0.0071 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | BRC 4D-TO24-002035.015-080324.pdf
BRC 96 FLATS Humidity: 46% | 16448/1 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | VOLTAMP Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 61 | 19 |  | ND | 101.60 | 9.771 | 0.0030 | 0.0294 | ND | 0.0832 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria except IFT test. $ ¦ Recommended frequency of testing is once in a year. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | BRC 96 FLATSTR-1TO24-002035.005-080324.pdf
BRC 96 FLATS Humidity: 46% | 12251 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | ETE Near Hotel Leela, Sahar Airport Road, $ | 1000kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 69 | 11 |  | ND | 1109.60 | 99.05 | 0.0017 | 0.0155 | 33 | 0.0159 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | BRC 96 FLATSTR-2TO24-002035.006-080324.pdf
BRC Badhrinath Humidity: 46% | 4444/51 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | BBL Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 51 | 29 |  | ND | 234.60 | 22.33 | 0.0012 | 0.0124 | ND | 0.0744 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria except IFT test. $ ¦ Recommended frequency of testing is once in a year. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | BRC Badhrinath-TO24-002035.014-080324.pdf
BRC Gulmarg Humidity: 46% | 42555/2 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | VOLTAMP Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 67 | 13 |  | ND | 7594.00 | 662 | 0.0009 | 0.0094 | 35 | 0.0142 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | BRC Gulmarg-TO24-002035.004-080324.pdf
BRC NPCIL Humidity: 46% | 4444/57 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | BBL Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 44 | ND |  | ND | 1784.00 | 162.4 | 0.0011 | 0.0115 | 27 | 0.0328 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria except water content test. $ ¦ Recommended frequency of testing is once in a year. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | BRC NPCILTR-1TO24-002035.010-080324.pdf
BRC NPCIL Humidity: 46% | 4444/70 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | BBL Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | ND | ND |  | ND | 844.30 | 78.99 | 0.0011 | 0.0125 | ND | 0.0691 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria except BDV, water content and IFT test. $ ¦ Recommended to recondition the oil. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | BRC NPCILTR-2TO24-002035.011-080324.pdf
BRC Pump Humidity: 46% | 42555/1 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | VOLTAMP Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 52 | 29 |  | ND | 259.90 | 247.7 | 0.0010 | 0.0105 | 32 | 0.0169 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | BRC Pump-TO24-002035.003-080324.pdf
GODREJ GREEN VILLA Humidity: 45% | M2653/1 Andheri east, Mumbai 400059. | 11/03/2024 | 08/03/2024 | CG-POWER Near Hotel Leela, Sahar Airport Road, $ | 750kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 57 | 23 |  | ND | 43.90 | 3.966 | 0.0050 | 0.0525 | ND | 0.0681 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria except IFT test. $ ¦ Recommended frequency of testing is once in a year. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | GODREJ GREEN VILLA-TO24-002116.010-110324.pdf
GODREJ HILL Humidity: 46% | 547 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | EMCO Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | ND | ND |  | ND | 13.70 | ND | 0.0120 | ND | ND | ND | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are not in the limits of Good criteria. $ ¦ Recommended to recondition the oil. ¦ DGA test results indicates presence of key gases. ¦ Recommends to carry out within three months to monitor rate of rise of individual gases. | GODREJ HILLTR-1TO24-002035.001-080324.pdf
GODREJ HILL Humidity: 46% | 547 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | EMCO Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 37 | ND |  | ND | 27.30 | ND | 0.0058 | ND | ND | ND | 1866 | 1448 |  | ND | ND | ND | ND | ND | ND | ND | ND | ND |  |  |  |  | Tested oil parameter results are not in the limits of Good criteria except BDV test. $ ¦ Recommended to recondition the oil. ¦ DGA test results indicates presence of key gases. ¦ Recommends to carry out within three months to monitor rate of rise of individual gases. | GODREJ HILLTR-1TO24-002035.002-080324.pdf
HDIL-1 Humidity: 45% | 04PMF004/31 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | KIRLOSKAR Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 65 | ND |  | ND | 14.66 | ND | 0.0010 | ND | ND | 0.1239 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are not in the limits of Good criteria except BDV and acidity test. $ ¦ Recommended to recondition the oil. ¦ DGA test results indicates presence of key gases. ¦ Recommends to carry out within three months to monitor rate of rise of individual gases. | HDIL-1TR-1TO24-002037.009-110324.pdf
HDIL-1 Humidity: 45% | 04PMF004/30 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | KIRLOSKAR Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 69 | 11 |  | ND | 49167.00 | 4547 | 0.0002 | 0.0009 | 37 | 0.0081 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | HDIL-1TR-2TO24-002037.011-110324.pdf
HDIL-3 Humidity: 45% | 04PMF004/25 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | KIRLOSKAR Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/440V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 74 | 7 |  | ND | 50196.00 | 4709 | 0.0003 | 0.0009 | 37 | 0.0070 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | HDIL-3TR-1TO24-002037.005-110324.pdf
HDIL-3 Humidity: 45% | 04PMF004/26 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | KIRLOSKAR Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/440V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 70 | 10 |  | ND | 11649.00 | 970.5 | 0.0005 | 0.0043 | 36 | 0.0081 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | HDIL-3TR-2TO24-002037.007-110324.pdf
HDIL-5 Humidity: 45% | 44545/3 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | VOLTAMP Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11kV/440V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 78 | 5 |  | ND | 18119.00 | 1605 | 0.0003 | 0.0007 | 37 | 0.0082 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | HDIL-5 TR-1TO24-002037.004-110324.pdf
HDIL Humidity: 45% | DT-3040/00 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | CG-POWER Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11kV/440V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 73 | 8 |  | ND | 13196.00 | 1125 | 0.0003 | 0.0021 | 36 | 0.0075 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | HDILTR-1TO24-002037.001-110324.pdf
HDIL Humidity: 45% | DT-3040/01 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | CG-POWER Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11kV/440V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 68 | 12 |  | ND | 59687.00 | 579.6 | 0.0005 | 0.0050 | 36 | 0.0076 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | HDILTR-2TO24-002037.002-110324.pdf
HDIL Humidity: 45% | 44545/5 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | VOLTAMP Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11kV/440V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 78 | 6 |  | ND | 50391.00 | 4449 | 0.0004 | 0.0009 | 36 | 0.0071 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | HDILTR-5TO24-002037.003-110324.pdf
HOLY FAMILY Humidity: 45% | DT2430/02 Andheri east, Mumbai 400059. | 11/03/2024 | 08/03/2024 | CG-POWER Near Hotel Leela, Sahar Airport Road, $ | 630kVA $ | 11kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 70 | 10 |  | ND | 741.60 | 528.7 | 0.0010 | 0.0095 | 36 | 0.0095 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | HOLY FAMILY-TO24-002116.009-110324.pdf
KANCHANGANGA Humidity: 46% | V2325/3 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | CG Near Hotel Leela, Sahar Airport Road, $ | 11kV/433V $ | 1250kVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 50 | ND |  | ND | 33.80 | 4.611 | 0.0034 | 0.0333 | ND | ND | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria except water content, acidity and IFT test. $ ¦ Recommended frequency of testing is once in a year. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | KANCHANGANGA--TO24-002257.009-270324.pdf
LAKDAWALA Humidity: 47% | ADA1610009-001 Andheri east, Mumbai 400059. | 28/03/2024 | 13/03/2024 | RAYCHEM Near Hotel Leela, Sahar Airport Road, $ | 630kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 70 | 10 |  | ND | 149.80 | 12.57 | 0.0006 | 0.0081 | 36 | 0.0100 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | LAKDAWALA--TO24-002281.009-280324.pdf
LAKDAWALA Humidity: 47% | ADA1613007-001 Andheri east, Mumbai 400059. | 28/03/2024 | 13/03/2024 | RAYCHEM Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 68 | 12 |  | ND | 23693.00 | 2232 | 0.0003 | 0.0011 | 36 | 0.0103 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | LAKDAWALA--TO24-002281.011-280324.pdf
MAIN PUMP-2 Humidity: 46% | V9325/4 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | CG Near Hotel Leela, Sahar Airport Road, $ | 11kV/433V $ | 1250kVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 55 | 25 |  | ND | 94.60 | 8.198 | 0.0020 | 0.0197 | ND | 0.1208 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria IFT test. $ ¦ Recommended frequency of testing is once in a year. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | MAIN PUMP-2 TR-1TO24-002257.006-270324.pdf
MANGALMURTI Humidity: 47% | 442 Andheri east, Mumbai 400059. | 28/03/2024 | 13/03/2024 | EMCO Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 70 | 10 |  | ND | 1944.60 | 171.5 | 0.0015 | 0.0137 | 36 | 0.0076 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | MANGALMURTI--TO24-002281.003-280324.pdf
Market City Humidity: 46% | 097G018/01 Andheri east, Mumbai 400059. | 25/01/2024 | 17/01/2024 | Kirloskar Near Hotel Leela, Sahar Airport Road, $ | 20MVA $ | 33/11 KV Temperature: 250C | Transformer Oil Center of Procurement Excellence , $ | 58 | 22 |  | ND | ND | 58.21 | ND | 0.0083 | 26 | 0.0395 | 0.02 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. ¦ Recommended frequency of testing is once in two years. $ ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | Market City DSS TRF 2.pdf
MARKET CITY Humidity: 45% | 09PH0034/02 Andheri east, Mumbai 400059. | 11/03/2024 | 08/03/2024 | KIRLOSKAR Near Hotel Leela, Sahar Airport Road, $ | 440kVA $ | 11kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 73 | 8 |  | ND | 7869.00 | 721.7 | 0.0006 | 0.0061 | 36 | 0.0118 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | MARKET CITY Stn TRF TR-1TO24-002116.007-110324.pdf
MARKET CITY Humidity: 45% | 09PH0034/01 Andheri east, Mumbai 400059. | 11/03/2024 | 08/03/2024 | KIRLOSKAR Near Hotel Leela, Sahar Airport Road, $ | 440kVA $ | 11kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 62 | 18 |  | ND | 191.60 | 17.22 | 0.0030 | 0.0338 | 28 | 0.0247 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | MARKET CITY STN TRF TR-2TO24-002116.008-110324.pdf
Market City Humidity: 46% | AFB-002 Andheri east, Mumbai 400059. | 25/01/2024 | 17/01/2024 | ABB Near Hotel Leela, Sahar Airport Road, $ | 20MVA $ | 33/11 KV Temperature: 250C | Transformer Oil Center of Procurement Excellence , $ | 80 | 4 |  | ND | ND | 2715 | ND | 0.0079 | 36 | 0.0098 | 0.02 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. ¦ Recommended frequency of testing is once in two years. $ ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | MARKET CITY TRF 1.pdf
MIAL NERSSERY Humidity: 45% | A0A1610011.00 Andheri east, Mumbai 400059. | 11/03/2024 | 08/03/2024 | RAYCHEM Near Hotel Leela, Sahar Airport Road, $ | 630kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 77 | 6 |  | ND | 521.60 | 48.45 | 0.0008 | 0.0069 | 36 | 0.0073 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | MIAL NERSSERY-TO24-002116.003-110324.pdf
NEW MANDALA Humidity: 46% | 11041 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | ETE Near Hotel Leela, Sahar Airport Road, $ | 11kV/433V $ | 1250kVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | ND | ND |  | ND | 8.14 | ND | 0.0220 | ND | ND | ND | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are not in the limits of Good criteria. $ ¦ Recommended to recondition the oil. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | NEW MANDALA TR-1TO24-002257.010-270324.pdf
NEW MANDALA Humidity: 46% | 11042 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | ETE Near Hotel Leela, Sahar Airport Road, $ | 11kV/433V $ | 1250kVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | ND | ND |  | ND | 1061.40 | 9.072 | 0.0021 | 0.0197 | ND | ND | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are not in the limits of Good criteria except Tan Delta and Resistivity test. $ ¦ Recommended to recondition the oil. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | NEW MANDALA TR-2TO24-002257.011-270324.pdf
NILGIRI Humidity: 46% | 84118 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | BRENTFORD Near Hotel Leela, Sahar Airport Road, $ | 11kV/433V $ | 1250kVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 52 | 28 |  | ND | 101.60 | 9.345 | 0.0035 | 0.0336 | ND | 0.0872 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria except IFT test. $ ¦ Recommended frequency of testing is once in a year. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | NILGIRI TR-1TO24-002257.007-270324.pdf
NILGIRI Humidity: 46% | 84117 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | BRENTFORD Near Hotel Leela, Sahar Airport Road, $ | 11kV/433V $ | 1250kVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | ND | ND |  | ND | 62.90 | 5.345 | 0.0031 | 0.0298 | ND | ND | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are not in the limits of Good criteria except Tan Delta and Resistivity test. $ ¦ Recommended to recondition the oil. ¦ DGA test results indicates presence of key gases. ¦ Recommends to carry out within three months to monitor rate of rise of individual gases. | NILGIRI TR-2TO24-002257.008-270324.pdf
Pestom Sagar DSS Humidity: 46% | AJW-002 Andheri east, Mumbai 400059. | 25/01/2024 | 17/01/2024 | ABB Near Hotel Leela, Sahar Airport Road, $ | 20MVA $ | 33/11 KV Temperature: 250C | Transformer Oil Center of Procurement Excellence , $ | 81 | 4 |  | ND | ND | 1450 | ND | 0.0070 | 37 | 0.0063 | 0.02 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. ¦ Recommended frequency of testing is once in two years. $ ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | PESTOM SAGAR.pdf
POPULAR Humidity: 45% | 1042 Andheri east, Mumbai 400059. | 11/03/2024 | 04/03/2024 | EMCO Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 55 | 25 |  | ND | 223.60 | 21.87 | 0.0020 | 0.0211 | 26 | 0.0374 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | POPULAR -TO24-002037.017-110324.pdf
RAGMALA Humidity: 46% | V9325/1 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | CG Near Hotel Leela, Sahar Airport Road, $ | 11kV/433V $ | 1000kVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 65 | 15 |  | ND | 1999.60 | 185.4 | 0.0006 | 0.0048 | 36 | 0.0127 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | RAGMALA TR-1TO24-002257.012-270324.pdf
SHABRI MOTIBAGH Humidity: 47% | 5155 Andheri east, Mumbai 400059. | 28/03/2024 | 13/03/2024 | TELAWANE Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 73 | 8 |  | ND | 3694.00 | 301 | 0.0008 | 0.0060 | 36 | 0.0135 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | SHABRI MOTIBAGH--TO24-002281.006-280324.pdf
SMS ENVOCLEAN Humidity: 47% | 24061 Andheri east, Mumbai 400059. | 28/03/2024 | 13/03/2024 | ON LOAD GEARS Near Hotel Leela, Sahar Airport Road, $ | 630kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 62 | 18 |  | ND | 399.60 | 33.67 | 0.0028 | 0.0272 | 35 | 0.0074 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | SMS ENVOCLEAN--TO24-002281.001-280324.pdf
V.S BHAVAN Humidity: 46% | RY-3094 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | VOLTAMP Near Hotel Leela, Sahar Airport Road, $ | 11kV/433V $ | 1000kVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 62 | 18 |  | ND | 154.60 | 14.06 | 0.0014 | 0.0144 | ND | 0.1095 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria except IFT test. $ ¦ Recommended frequency of testing is once in a year. ¦ DGA test results indicates presence of key gases. ¦ Recommends to carry out within three months to monitor rate of rise of individual gases. | V.S BHAVAN--TO24-002257.013-270324.pdf
VRINDAVAN Humidity: 46% | AFB-001 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | ABB Near Hotel Leela, Sahar Airport Road, $ | 22/11kV $ | 20MVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 77 | 6 |  | ND | 26796.00 | 2371 | 0.0003 | 0.0006 | 36 | 0.0081 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | VRINDAVAN DT-1TO24-002257.001-270324.pdf
VRINDAVAN Humidity: 46% | AFB-005 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | ABB Near Hotel Leela, Sahar Airport Road, $ | 22/11kV $ | 20MVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 74 | 7 |  | ND | 3999.00 | 351.8 | 0.0008 | 0.0066 | 36 | 0.0090 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | VRINDAVAN DT-2TO24-002257.003-270324.pdf
VRINDAVAN Humidity: 46% | RDM-5088/1 Andheri east, Mumbai 400059. | 27/03/2024 | 11/03/2024 | CG Near Hotel Leela, Sahar Airport Road, $ | 11kV/433V $ | 300kVA Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 73 | 8 |  | ND | 16196.00 | 1401 | 0.0004 | 0.0028 | 36 | 0.0103 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | VRINDAVAN STN TRFTO24-002257.005-270324.pdf
Western Sector Humidity: 46% | 4444/61 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | BBL Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 52 | 28 |  | ND | 945.40 | 86.48 | 0.0016 | 0.0158 | 27 | 0.0316 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | Western Sector-TO24-002035.012-080324.pdf
Western Sector Humidity: 46% | 4444/71 Andheri east, Mumbai 400059. | 08/03/2024 | 01/03/2024 | BBL Near Hotel Leela, Sahar Airport Road, $ | 1250kVA $ | 11/0.433kV Temperature: 25 °C | Transformer Oil Center of Procurement Excellence , $ | 52 | 29 |  | ND | 855.70 | 76.95 | 0.0012 | 0.0125 | ND | 0.0635 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria except IFT test. $ ¦ Recommended frequency of testing is once in a year. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | Western Sector-TO24-002035.013-080324.pdf
YOGAYATANI Humidity: 47% | JF032/01 Andheri east, Mumbai 400059. | 28/03/2024 | 13/03/2024 | KIRLOSKAR Near Hotel Leela, Sahar Airport Road, $ | 630kVA $ | 22kV/433V Temperature: 26 °C | Transformer Oil Center of Procurement Excellence , $ | 69 | 11 |  | ND | 13692.00 | 1074 | 0.0005 | 0.0035 | 36 | 0.0096 | 1866 | 1448 |  | 50 | ND | ND | 400 | 30 | 3800 | 60 | 20 | 2 |  |  |  |  | Tested oil parameter results are within the limits of Good criteria. $ ¦ Recommended frequency of testing is once in two years. ¦ DGA test results indicates that normal functioning of transformer. ¦ Recommends to carry out annually to monitor rate of rise of individual gases. | YOGAYATANI--TO24-002281.004-280324.pdf
96 FLAT | TR#1 | 11-02-2026 | 04-01-2026 | Voltamp Transformers Limited | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 56 | 36 | L 7.0 | 2 | 13.90 | 1.11 | ND | ND | ND | 3 | 1 | 5 | ND | 0.25 | 1492.70 | 47780.00 | 29.85 | 0.55 | 724.85 | 2.45 | 0.55 | ND | 0.35 | 0.40 | 34 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | 96_Flat_TRF-1_1.pdf
96 FLAT | TR#1 | 11-02-2026 | 04-01-2026 | Voltamp Transformers Limited | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 56 | 36 | L 7.0 | 2 | 13.90 | 1.11 | ND | ND | ND | 3 | 1 | 5 | ND | 0.25 | 1492.70 | 47780.00 | 29.85 | 0.55 | 724.85 | 2.45 | 0.55 | ND | 0.35 | 0.40 | 34 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | 96_Flat_TRF-1_1_1.pdf
Aacharya Udyog | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 73 | 14 | L 7.0 | 0 | 99.44 | 8.31 | ND | ND | ND | 3 | 1 | 5 | 945 | 0.38 | 1627.78 | 51749.39 | 29.59 | 0.97 | 645.08 | 0.38 | 0.97 | ND | 0.32 | 0.32 | 32.12 | 5.4 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Aacharya_Udyog_TRF-1_1.pdf
Aacharya Udyog | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 73 | 14 | L 7.0 | 0 | 99.44 | 8.31 | ND | ND | ND | 3 | 1 | 5 | 945 | 0.38 | 1627.78 | 51749.39 | 29.59 | 0.97 | 645.08 | 0.38 | 0.97 | ND | 0.32 | 0.32 | 32.12 | 5.4 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Aacharya_Udyog_TRF-1_1_1.pdf
Aacharya Udyog | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 63 | 23 | L 7.0 | 1 | 189.28 | 14.07 | ND | ND | ND | 3 | 1 | 5 | 1079 | 10.08 | 1287.54 | 43083.00 | 74.61 | 1.53 | 802.58 | 1.35 | 1.53 | ND | 0.14 | 0.14 | 87.99 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Aacharya_Udyog_TRF-1_2.pdf
Aacharya Udyog | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 63 | 23 | L 7.0 | 1 | 189.28 | 14.07 | ND | ND | ND | 3 | 1 | 5 | 1079 | 10.08 | 1287.54 | 43083.00 | 74.61 | 1.53 | 802.58 | 1.35 | 1.53 | ND | 0.14 | 0.14 | 87.99 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Aacharya_Udyog_TRF-1_2_1.pdf
ADDRESS | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd |  | 36 KV | Dielectric Fluid-Mineral Base | 65 | 18 | L 7.0 | 2 | 149.73 | 12.71 | ND | ND | ND | 3 | 1 | 5 | 1075 | 1.09 | 656.39 | 31826.79 | 407.79 | 3.15 | 1356.74 | 2.07 | 3.15 | ND | 0.14 | 0.14 | 414.77 | 3.5 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Address_DT-1_1.pdf
ADDRESS | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd |  | 36 KV | Dielectric Fluid-Mineral Base | 65 | 18 | L 7.0 | 2 | 149.73 | 12.71 | ND | ND | ND | 3 | 1 | 5 | 1075 | 1.09 | 656.39 | 31826.79 | 407.79 | 3.15 | 1356.74 | 2.07 | 3.15 | ND | 0.14 | 0.14 | 414.77 | 3.5 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Address_DT-1_1_1.pdf
ADDRESS | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd |  | 36 KV | Dielectric Fluid-Mineral Base | 66 | 20 | L 7.0 | 9 | 2350.40 | 64.98 | ND | ND | ND | 3 | 1 | 5 | 526 | 987.98 | 31703.31 | 31703.31 | 26.46 | 5.88 | 172.24 | 4.97 | 5.88 | 24.19 | 0.28 | 0.28 | 1050.25 | 3.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Address_DT-1_2.pdf
ADDRESS | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd |  | 36 KV | Dielectric Fluid-Mineral Base | 66 | 20 | L 7.0 | 9 | 2350.40 | 64.98 | ND | ND | ND | 3 | 1 | 5 | 526 | 987.98 | 31703.31 | 31703.31 | 26.46 | 5.88 | 172.24 | 4.97 | 5.88 | 24.19 | 0.28 | 0.28 | 1050.25 | 3.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Address_DT-1_2_1.pdf
Address- | DT-2 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 65 | 22 | L 7.0 | 3 | 717.55 | 102.83 | ND | ND | ND | 3 | 1 | 5 | 1060 | 934.25 | 1294.07 | 32048.58 | 60.98 | 66.60 | 310.10 | 61.26 | 66.60 | 260.33 | 3.02 | 3.02 | 1391.8 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Address_DT-2_1.pdf
Address- | DT-2 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 65 | 22 | L 7.0 | 3 | 717.55 | 102.83 | ND | ND | ND | 3 | 1 | 5 | 1060 | 934.25 | 1294.07 | 32048.58 | 60.98 | 66.60 | 310.10 | 61.26 | 66.60 | 260.33 | 3.02 | 3.02 | 1391.8 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Address_DT-2_1_1.pdf
Address- | DT-2 | 21-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 66 | 21 | L 7.0 | 5 | 90.97 | 5.99 | ND | ND | ND | 3 | 1 | 5 | 1070 | 0.69 | 1498.37 | 46901.62 | 259.21 | 3.48 | 739.61 | 0.05 | 3.48 | ND | 0.05 | 0.05 | 263.78 | 4.9 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Address_DT-2_2.pdf
Address- | DT-2 | 21-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 66 | 21 | L 7.0 | 5 | 90.97 | 5.99 | ND | ND | ND | 3 | 1 | 5 | 1070 | 0.69 | 1498.37 | 46901.62 | 259.21 | 3.48 | 739.61 | 0.05 | 3.48 | ND | 0.05 | 0.05 | 263.78 | 4.9 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Address_DT-2_2_1.pdf
Akash Ganga | TR#1 | 21-02-2026 | 04-01-2026 | ETE | 1000 KVA | 12 KV | Dielectric Fluid-Mineral Base | 24 | 85 | L 7.0 | 1 | 1.71 | 0.28 | ND | ND | ND | 3 | 1 | 5 | 45 | 12.52 | 999.60 | 40253.05 | 187.11 | 1.60 | 1709.06 | 2.31 | 1.60 | ND | 0.84 | 0.84 | 205.6 | 4.2 | The oil is heavily contaminated with acidic impurities and is UNFIT for retention in the transformer. The resistivity value is below the | Akash_ganga-TRF-1_1.pdf
Akash Ganga | TR#1 | 21-02-2026 | 04-01-2026 | ETE | 1000 KVA | 12 KV | Dielectric Fluid-Mineral Base | 24 | 85 | L 7.0 | 1 | 1.71 | 0.28 | ND | ND | ND | 3 | 1 | 5 | 45 | 12.52 | 999.60 | 40253.05 | 187.11 | 1.60 | 1709.06 | 2.31 | 1.60 | ND | 0.84 | 0.84 | 205.6 | 4.2 | The oil is heavily contaminated with acidic impurities and is UNFIT for retention in the transformer. The resistivity value is below the | Akash_ganga-TRF-1_1_1.pdf
Akash Ganga | TR#1 | 21-02-2026 | 04-01-2026 | ETE | 1000 KVA | 12 KV | Dielectric Fluid-Mineral Base | 24 | 85 | L 7.0 | 1 | 1.71 | 0.28 | ND | ND | ND | 3 | 1 | 5 | 45 | 12.52 | 999.60 | 40253.05 | 187.11 | 1.60 | 1709.06 | 2.31 | 1.60 | ND | 0.84 | 0.84 | 205.6 | 4.2 | The oil is heavily contaminated with acidic impurities and is UNFIT for retention in the transformer. The resistivity value is below the | Akash_ganga-TRF-1_2.pdf
Akash Ganga | TR#1 | 21-02-2026 | 04-01-2026 | ETE | 1000 KVA | 12 KV | Dielectric Fluid-Mineral Base | 24 | 85 | L 7.0 | 1 | 1.71 | 0.28 | ND | ND | ND | 3 | 1 | 5 | 45 | 12.52 | 999.60 | 40253.05 | 187.11 | 1.60 | 1709.06 | 2.31 | 1.60 | ND | 0.84 | 0.84 | 205.6 | 4.2 | The oil is heavily contaminated with acidic impurities and is UNFIT for retention in the transformer. The resistivity value is below the | Akash_ganga-TRF-1_2_1.pdf
Akash Ratnadeep | TR#2 | 11-02-2026 | 04-01-2026 | Bharat Bijlee Limited | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 62 | 16 | L 7.0 | 5 | 74.02 | 9.49 | ND | ND | ND | 3 | 1 | 5 | 1103 | 2.12 | 1324.67 | 43097.36 | 66.11 | 1.08 | 550.53 | 0.27 | 1.08 | ND | 0.14 | 0.18 | 70.04 | 4.5 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Akashratnadeep_TRF-2_1.pdf
Akash Ratnadeep | TR#2 | 11-02-2026 | 04-01-2026 | Bharat Bijlee Limited | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 62 | 16 | L 7.0 | 5 | 74.02 | 9.49 | ND | ND | ND | 3 | 1 | 5 | 1103 | 2.12 | 1324.67 | 43097.36 | 66.11 | 1.08 | 550.53 | 0.27 | 1.08 | ND | 0.14 | 0.18 | 70.04 | 4.5 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Akashratnadeep_TRF-2_1_1.pdf
Amar interprises | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 750 KVA | 24 KV | Dielectric Fluid-Mineral Base | 64 | 24 | L 7.0 | 8 | 8.64 | 0.92 | ND | ND | ND | 3 | 1 | 5 | ND | 0.91 | 918.43 | 45727.39 | 310.56 | 8.50 | 1076.21 | 2.35 | 8.50 | ND | 1.30 | 1.34 | 326.69 | 4.8 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | AmarEnterprise_TRF-1_1.pdf
Amar interprises | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 750 KVA | 24 KV | Dielectric Fluid-Mineral Base | 64 | 24 | L 7.0 | 8 | 8.64 | 0.92 | ND | ND | ND | 3 | 1 | 5 | ND | 0.91 | 918.43 | 45727.39 | 310.56 | 8.50 | 1076.21 | 2.35 | 8.50 | ND | 1.30 | 1.34 | 326.69 | 4.8 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | AmarEnterprise_TRF-1_1_1.pdf
Amar interprises | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 750 KVA | 24 KV | Dielectric Fluid-Mineral Base | 28 | 46 | L 7.0 | 5 | 3.85 | 0.27 | ND | ND | ND | 3 | 1 | 5 | ND | 8.19 | 508.27 | 33459.13 | 314.41 | 14.28 | 1020.43 | 3.15 | 14.28 | 5.36 | 1.30 | 1.30 | 350.06 | 3.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | AmarEnterprise_TRF-1_2.pdf
Amar interprises | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 750 KVA | 24 KV | Dielectric Fluid-Mineral Base | 28 | 46 | L 7.0 | 5 | 3.85 | 0.27 | ND | ND | ND | 3 | 1 | 5 | ND | 8.19 | 508.27 | 33459.13 | 314.41 | 14.28 | 1020.43 | 3.15 | 14.28 | 5.36 | 1.30 | 1.30 | 350.06 | 3.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | AmarEnterprise_TRF-1_2_1.pdf
Backbay DSS | DT-1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 73 | 15 | L 7.0 | 6 | 289.85 | 25.03 | ND | ND | ND | 3 | 1 | 5 | 915 | 2.71 | 1132.36 | 41083.53 | 74.61 | 2.32 | 418.99 | 0.82 | 2.32 | ND | 0.17 | 0.17 | 81.02 | 4.3 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Back_bay_DT-1_1.pdf
Backbay DSS | DT-1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 73 | 15 | L 7.0 | 6 | 289.85 | 25.03 | ND | ND | ND | 3 | 1 | 5 | 915 | 2.71 | 1132.36 | 41083.53 | 74.61 | 2.32 | 418.99 | 0.82 | 2.32 | ND | 0.17 | 0.17 | 81.02 | 4.3 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Back_bay_DT-1_1_1.pdf
BARC / 1250 KVA TRANSFORMER |  | 11-02-2026 | 04-01-2026 | Bharat Bijlee Limited | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 64 | 20 | L 7.0 | 8 | 168.93 | 13.90 | ND | ND | ND | 3 | 1 | 5 | 1034 | 17.04 | 1369.60 | 38294.80 | 91.12 | 0.84 | 2204.16 | 1.32 | 0.84 | ND | 0.36 | 0.36 | 111.4 | 4.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | BARC_TRF-1_1.pdf
BARC / 1250 KVA TRANSFORMER |  | 11-02-2026 | 04-01-2026 | Bharat Bijlee Limited | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 64 | 20 | L 7.0 | 8 | 168.93 | 13.90 | ND | ND | ND | 3 | 1 | 5 | 1034 | 17.04 | 1369.60 | 38294.80 | 91.12 | 0.84 | 2204.16 | 1.32 | 0.84 | ND | 0.36 | 0.36 | 111.4 | 4.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | BARC_TRF-1_1_1.pdf
CHANDIVALI-LIGHT HALL / 20 MVA |  | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 60 | 17 | L 7.0 | 0 | 1045.25 | 98.76 | ND | ND | ND | 3 | 1 | 5 | 1260 | 946.08 | 983.99 | 31642.86 | 26.71 | 53.24 | 149.94 | 47.34 | 53.24 | 206.46 | 2.16 | 2.16 | 1286.06 | 3.60 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Chandivali_Light_hall_DT-1_1.pdf
CHANDIVALI-LIGHT HALL / 20 MVA |  | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 60 | 17 | L 7.0 | 0 | 1045.25 | 98.76 | ND | ND | ND | 3 | 1 | 5 | 1260 | 946.08 | 983.99 | 31642.86 | 26.71 | 53.24 | 149.94 | 47.34 | 53.24 | 206.46 | 2.16 | 2.16 | 1286.06 | 3.60 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Chandivali_Light_hall_DT-1_1_1.pdf
GLENDER CROFT | TR-1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 78 | 18 | L 7.0 | 6 | 159.33 | 10.90 | ND | ND | ND | 3 | 1 | 5 | 715 | 1.65 | 1513.00 | 32356.65 | 90.80 | 0.70 | 1103.60 | 1.85 | 0.70 | ND | 0.40 | 0.40 | 95.95 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Glen_Crof_TRF-1_1.pdf
GLENDER CROFT | TR-1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 78 | 18 | L 7.0 | 6 | 159.33 | 10.90 | ND | ND | ND | 3 | 1 | 5 | 715 | 1.65 | 1513.00 | 32356.65 | 90.80 | 0.70 | 1103.60 | 1.85 | 0.70 | ND | 0.40 | 0.40 | 95.95 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Glen_Crof_TRF-1_1_1.pdf
GLENDER CROFT | TR-1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 59 | 22 | L 7.0 | 7 | 296.62 | 21.02 | ND | ND | ND | 3 | 1 | 5 | 1042 | 6.20 | 1140.66 | 32150.37 | 118.49 | 4.09 | 587.27 | 4.75 | 4.09 | 5.28 | 0.26 | 0.26 | 139.59 | 4.4 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Glen_Croft_TRF-1_2.pdf
GLENDER CROFT | TR-1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 59 | 22 | L 7.0 | 7 | 296.62 | 21.02 | ND | ND | ND | 3 | 1 | 5 | 1042 | 6.20 | 1140.66 | 32150.37 | 118.49 | 4.09 | 587.27 | 4.75 | 4.09 | 5.28 | 0.26 | 0.26 | 139.59 | 4.4 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Glen_Croft_TRF-1_2_1.pdf
GODREJ DSS | DT-1 | 22-02-2026 | 04-01-2026 | Godrej Industries Limited |  | 12 KV | Dielectric Fluid-Mineral Base | 75 | 15 | L 7.0 | 6 | 104.53 | 6.05 | ND | ND | ND | 3 | 1 | 5 | 888 | 0.38 | 1430.02 | 45859.20 | 25.20 | 1.73 | 401.71 | 3.07 | 1.73 | 9.79 | 0.14 | 0.19 | 40.64 | 4.8 | The oil is fit for use in the equipment, and no corrective action is required at this time. No fault is detected from the gas analysis; | Godrej_DT_1_2.pdf
GODREJ DSS | DT-1 | 22-02-2026 | 04-01-2026 | Godrej Industries Limited |  | 12 KV | Dielectric Fluid-Mineral Base | 75 | 15 | L 7.0 | 6 | 104.53 | 6.05 | ND | ND | ND | 3 | 1 | 5 | 888 | 0.38 | 1430.02 | 45859.20 | 25.20 | 1.73 | 401.71 | 3.07 | 1.73 | 9.79 | 0.14 | 0.19 | 40.64 | 4.8 | The oil is fit for use in the equipment, and no corrective action is required at this time. No fault is detected from the gas analysis; | Godrej_DT_1_2_1.pdf
GODREJ DSS | DT-1 | 11-02-2026 | 04-01-2026 | Godrej Industries Limited |  | 12 KV | Dielectric Fluid-Mineral Base | 73 | 17 | L 7.0 | 5 | 222.05 | 26.33 | ND | ND | ND | 3 | 1 | 5 | 921 | 306.72 | 1272.93 | 31985.48 | 31.18 | 21.41 | 352.99 | 17.72 | 21.41 | 112.70 | 0.95 | 0.95 | 492.32 | 4.3 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Godrej_DT-1_1.pdf
GODREJ DSS | DT-1 | 11-02-2026 | 04-01-2026 | Godrej Industries Limited |  | 12 KV | Dielectric Fluid-Mineral Base | 73 | 17 | L 7.0 | 5 | 222.05 | 26.33 | ND | ND | ND | 3 | 1 | 5 | 921 | 306.72 | 1272.93 | 31985.48 | 31.18 | 21.41 | 352.99 | 17.72 | 21.41 | 112.70 | 0.95 | 0.95 | 492.32 | 4.3 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Godrej_DT-1_1_1.pdf
GODREJ DSS | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 12 KV | Dielectric Fluid-Mineral Base | 63 | 17 | L 7.0 | 9 | 179.67 | 12.20 | ND | ND | ND | 3 | 1 | 5 | 1077 | 54.00 | 1186.17 | 39231.92 | 16.24 | 4.63 | 509.88 | 5.21 | 4.63 | 48.30 | 0.37 | 0.41 | 129.61 | 4.1 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Godrej_DT-2_1.pdf
GODREJ DSS | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 12 KV | Dielectric Fluid-Mineral Base | 63 | 17 | L 7.0 | 9 | 179.67 | 12.20 | ND | ND | ND | 3 | 1 | 5 | 1077 | 54.00 | 1186.17 | 39231.92 | 16.24 | 4.63 | 509.88 | 5.21 | 4.63 | 48.30 | 0.37 | 0.41 | 129.61 | 4.1 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Godrej_DT-2_1_1.pdf
GODREJ DSS | DT-2 | 21-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 12 KV | Dielectric Fluid-Mineral Base | 76 | 14 | L 7.0 | 8 | 988.75 | 98.25 | ND | ND | ND | 3 | 1 | 5 | 967 | 0.30 | 1477.35 | 47725.95 | 30.80 | 1.15 | 431.35 | 1.85 | 1.15 | 1.65 | 0.15 | 0.20 | 36.2 | 5.0 | The oil is fit for use in the equipment, and no corrective action is required at this time. No fault is detected from the gas analysis; | Godrej_DT-2_2.pdf
GODREJ DSS | DT-2 | 21-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 12 KV | Dielectric Fluid-Mineral Base | 76 | 14 | L 7.0 | 8 | 988.75 | 98.25 | ND | ND | ND | 3 | 1 | 5 | 967 | 0.30 | 1477.35 | 47725.95 | 30.80 | 1.15 | 431.35 | 1.85 | 1.15 | 1.65 | 0.15 | 0.20 | 36.2 | 5.0 | The oil is fit for use in the equipment, and no corrective action is required at this time. No fault is detected from the gas analysis; | Godrej_DT-2_2_1.pdf
GODREJ STP | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 630 KVA | 24 KV | Dielectric Fluid-Mineral Base | 76 | 12 | L 7.0 | 1 | 180.24 | 15.93 | ND | ND | ND | 3 | 1 | 5 | 1061 | 0.35 | 1524.45 | 32358.75 | 49.00 | 1.40 | 593.85 | 0.55 | 1.40 | ND | 0.50 | 0.55 | 52.5 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Godrej_STP_TRF-1_1.pdf
GODREJ STP | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 630 KVA | 24 KV | Dielectric Fluid-Mineral Base | 76 | 12 | L 7.0 | 1 | 180.24 | 15.93 | ND | ND | ND | 3 | 1 | 5 | 1061 | 0.35 | 1524.45 | 32358.75 | 49.00 | 1.40 | 593.85 | 0.55 | 1.40 | ND | 0.50 | 0.55 | 52.5 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Godrej_STP_TRF-1_1_1.pdf
GODREJ STP | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 630 KVA | 24 KV | Dielectric Fluid-Mineral Base | 65 | 16 | L 7.0 | 1 | 206.23 | 17.91 | ND | ND | ND | 3 | 1 | 5 | 1019 | 0.55 | 1490.30 | 47844.05 | 45.25 | 2.85 | 596.15 | 0.15 | 2.85 | 0.25 | 0.10 | 0.10 | 49.45 | 5.0 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Godrej_STP_TRF-1_2.pdf
GODREJ STP | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 630 KVA | 24 KV | Dielectric Fluid-Mineral Base | 65 | 16 | L 7.0 | 1 | 206.23 | 17.91 | ND | ND | ND | 3 | 1 | 5 | 1019 | 0.55 | 1490.30 | 47844.05 | 45.25 | 2.85 | 596.15 | 0.15 | 2.85 | 0.25 | 0.10 | 0.10 | 49.45 | 5.0 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Godrej_STP_TRF-1_2_1.pdf
Hiranandani DSS | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 62 | 19 | L 7.0 | 5 | 10.28 | 1.38 | ND | ND | ND | 3 | 1 | 5 | 940 | 1438.26 | 605.62 | 35257.93 | 191.55 | 103.19 | 655.86 | 100.38 | 103.19 | 554.08 | 2.55 | 2.55 | 2396.37 | 3.7 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Hiranandani_DT-1_1.pdf
Hiranandani DSS | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 62 | 19 | L 7.0 | 5 | 10.28 | 1.38 | ND | ND | ND | 3 | 1 | 5 | 940 | 1438.26 | 605.62 | 35257.93 | 191.55 | 103.19 | 655.86 | 100.38 | 103.19 | 554.08 | 2.55 | 2.55 | 2396.37 | 3.7 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Hiranandani_DT-1_1_1.pdf
Hiranandani DSS | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 71 | 15 | L 7.0 | 3 | 153.68 | 33.56 | ND | ND | ND | 3 | 1 | 5 | 1017 | 1.92 | 613.93 | 25783.73 | 228.74 | 1.62 | 994.98 | 1.05 | 1.62 | ND | 0.05 | 0.05 | 233.59 | 2.7 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Hiranandani_DT-1_2.pdf
Hiranandani DSS | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 71 | 15 | L 7.0 | 3 | 153.68 | 33.56 | ND | ND | ND | 3 | 1 | 5 | 1017 | 1.92 | 613.93 | 25783.73 | 228.74 | 1.62 | 994.98 | 1.05 | 1.62 | ND | 0.05 | 0.05 | 233.59 | 2.7 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Hiranandani_DT-1_2_1.pdf
Hiranandani DSS | DT#2 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 75 | 13 | L 7.0 | 0 | 166.67 | 17.18 | ND | ND | ND | 3 | 1 | 5 | 1026 | 0.40 | 950.76 | 38045.00 | 254.32 | 2.24 | 1217.72 | 3.08 | 2.24 | ND | 0.04 | 0.08 | 260.28 | 4.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Hiranandani_DT-2_1.pdf
Hiranandani DSS | DT#2 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 75 | 13 | L 7.0 | 0 | 166.67 | 17.18 | ND | ND | ND | 3 | 1 | 5 | 1026 | 0.40 | 950.76 | 38045.00 | 254.32 | 2.24 | 1217.72 | 3.08 | 2.24 | ND | 0.04 | 0.08 | 260.28 | 4.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Hiranandani_DT-2_1_1.pdf
Hiranandani DSS | DT#2 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 64 | 16 | L 7.0 | 5 | 197.75 | 24.63 | ND | ND | ND | 3 | 1 | 5 | 986 | 205.15 | 620.48 | 23788.68 | 3.98 | 8.53 | 68.78 | 6.53 | 8.53 | 59.23 | 0.28 | 0.30 | 284.2 | 2.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Hiranandani_DT-2_2.pdf
Hiranandani DSS | DT#2 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 64 | 16 | L 7.0 | 5 | 197.75 | 24.63 | ND | ND | ND | 3 | 1 | 5 | 986 | 205.15 | 620.48 | 23788.68 | 3.98 | 8.53 | 68.78 | 6.53 | 8.53 | 59.23 | 0.28 | 0.30 | 284.2 | 2.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Hiranandani_DT-2_2_1.pdf
klick nixion | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 64 | 16 | L 7.0 | 3 | 402.85 | 16.27 | ND | ND | ND | 3 | 1 | 5 | 868 | 1572.00 | 1248.49 | 32099.16 | 142.05 | 144.35 | 285.89 | 130.73 | 144.35 | 312.66 | 8.60 | 8.60 | 2327.04 | 4.6 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Kilick_Nixon_DT-1_2.pdf
klick nixion | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 64 | 16 | L 7.0 | 3 | 402.85 | 16.27 | ND | ND | ND | 3 | 1 | 5 | 868 | 1572.00 | 1248.49 | 32099.16 | 142.05 | 144.35 | 285.89 | 130.73 | 144.35 | 312.66 | 8.60 | 8.60 | 2327.04 | 4.6 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Kilick_Nixon_DT-1_2_1.pdf
klick nixion | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 75 | 16 | L 7.0 | 3 | 128.26 | 16.27 | ND | ND | ND | 3 | 1 | 5 | 914 | 0.63 | 1008.68 | 43151.18 | 181.98 | 14.36 | 489.51 | 9.00 | 14.36 | ND | 3.83 | 3.83 | 225.38 | 4.5 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | KILLICK_NIXON_DT-1_1.pdf
klick nixion | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 75 | 16 | L 7.0 | 3 | 128.26 | 16.27 | ND | ND | ND | 3 | 1 | 5 | 914 | 0.63 | 1008.68 | 43151.18 | 181.98 | 14.36 | 489.51 | 9.00 | 14.36 | ND | 3.83 | 3.83 | 225.38 | 4.5 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | KILLICK_NIXON_DT-1_1_1.pdf
L & T | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | L&T_DT-1_1.pdf
L & T | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | L&T_DT-1_1_1.pdf
L & T | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | L&T_DT-1_2.pdf
L & T | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | L&T_DT-1_2_1.pdf
L&T | DT#2 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | L&T_DT-2_1.pdf
L&T | DT#2 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | L&T_DT-2_1_1.pdf
MARKET CITY | DT-1 | 11-02-2026 | 04-01-2026 | ABB |  | 36 KV | Dielectric Fluid-Mineral Base | 63 | 21 | L 7.0 | 0 | 762.75 | 197.75 | ND | ND | ND | 3 | 1 | 5 | 1122 | 1.02 | 679.11 | 32637.65 | 173.64 | 3.39 | 311.43 | 0.84 | 3.39 | ND | 0.12 | 0.15 | 179.94 | 3.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Market_City_DT-1_1.pdf
MARKET CITY | DT-1 | 11-02-2026 | 04-01-2026 | ABB |  | 36 KV | Dielectric Fluid-Mineral Base | 63 | 21 | L 7.0 | 0 | 762.75 | 197.75 | ND | ND | ND | 3 | 1 | 5 | 1122 | 1.02 | 679.11 | 32637.65 | 173.64 | 3.39 | 311.43 | 0.84 | 3.39 | ND | 0.12 | 0.15 | 179.94 | 3.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Market_City_DT-1_1_1.pdf
MARKET CITY | DT-1 | 11-02-2026 | 04-01-2026 | ABB |  | 36 KV | Dielectric Fluid-Mineral Base | 65 | 20 | L 7.0 | 9 | 100.01 | 10.72 | ND | ND | ND | 3 | 1 | 5 | 1067 | 1447.88 | 1352.98 | 31970.32 | 168.05 | 89.89 | 388.22 | 96.34 | 89.89 | 263.74 | 12.85 | 12.85 | 2129.94 | 3.6 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Market_City_DT-1_2.pdf
MARKET CITY | DT-1 | 11-02-2026 | 04-01-2026 | ABB |  | 36 KV | Dielectric Fluid-Mineral Base | 65 | 20 | L 7.0 | 9 | 100.01 | 10.72 | ND | ND | ND | 3 | 1 | 5 | 1067 | 1447.88 | 1352.98 | 31970.32 | 168.05 | 89.89 | 388.22 | 96.34 | 89.89 | 263.74 | 12.85 | 12.85 | 2129.94 | 3.6 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Market_City_DT-1_2_1.pdf
MARKET CITY | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 36 KV | Dielectric Fluid-Mineral Base | 75 | 16 | L 7.0 | 9 | 46.44 | 2.94 | ND | ND | ND | 3 | 1 | 5 | 959 | 992.52 | 1284.57 | 32113.11 | 38.84 | 64.49 | 236.75 | 62.24 | 64.49 | 275.81 | 4.32 | 4.32 | 1445.69 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Market_City_DT-2_1.pdf
MARKET CITY | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 36 KV | Dielectric Fluid-Mineral Base | 75 | 16 | L 7.0 | 9 | 46.44 | 2.94 | ND | ND | ND | 3 | 1 | 5 | 959 | 992.52 | 1284.57 | 32113.11 | 38.84 | 64.49 | 236.75 | 62.24 | 64.49 | 275.81 | 4.32 | 4.32 | 1445.69 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Market_City_DT-2_1_1.pdf
MARKET CITY | DT-2 | 22-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 36 KV | Dielectric Fluid-Mineral Base | 63 | 23 | L 7.0 | 0 | 361.04 | 16.95 | ND | ND | ND | 3 | 1 | 5 | 1002 | 0.26 | 1212.86 | 41025.31 | 41.80 | 2.41 | 651.19 | 1.03 | 2.41 | ND | 0.17 | 0.17 | 45.93 | 4.3 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Market_City_DT-2_2.pdf
MARKET CITY | DT-2 | 22-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 36 KV | Dielectric Fluid-Mineral Base | 63 | 23 | L 7.0 | 0 | 361.04 | 16.95 | ND | ND | ND | 3 | 1 | 5 | 1002 | 0.26 | 1212.86 | 41025.31 | 41.80 | 2.41 | 651.19 | 1.03 | 2.41 | ND | 0.17 | 0.17 | 45.93 | 4.3 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Market_City_DT-2_2_1.pdf
MARWAHA IND | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Marwah_Ind_TRF-1_1.pdf
MARWAHA IND | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Marwah_Ind_TRF-1_1_1.pdf
MARWAHA IND | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | 4.24 | 350.80 | 38293.72 | 89.48 | 3.64 | 782.24 | 4.48 | 3.64 | ND | 1.52 | 1.52 | 171.4 | 4.0 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Marwah_ind_TRF-1_2.pdf
MARWAHA IND | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | 4.24 | 350.80 | 38293.72 | 89.48 | 3.64 | 782.24 | 4.48 | 3.64 | ND | 1.52 | 1.52 | 171.4 | 4.0 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Marwah_ind_TRF-1_2_1.pdf
New Mandala | TR#1 | 21-02-2026 | 04-01-2026 | ETE | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 26 | 73 | L 7.0 | 1 | 0.63 | 0.11 | ND | ND | ND | 3 | 1 | 5 | 52 | 31.64 | 929.79 | 43164.27 | 206.37 | 4.37 | 3328.83 | 19.49 | 4.37 | ND | 2.39 | 2.43 | 267.64 | 4.5 | The oil is heavily contaminated with acidic impurities and is UNFIT for retention in the transformer. The resistivity value is below the | New_Mandala_TRF-1_1.pdf
New Mandala | TR#1 | 21-02-2026 | 04-01-2026 | ETE | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 26 | 73 | L 7.0 | 1 | 0.63 | 0.11 | ND | ND | ND | 3 | 1 | 5 | 52 | 31.64 | 929.79 | 43164.27 | 206.37 | 4.37 | 3328.83 | 19.49 | 4.37 | ND | 2.39 | 2.43 | 267.64 | 4.5 | The oil is heavily contaminated with acidic impurities and is UNFIT for retention in the transformer. The resistivity value is below the | New_Mandala_TRF-1_1_1.pdf
New Mandala | TR#2 | 11-02-2026 | 04-01-2026 | ETE | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 26 | 46 | L 7.0 | 2 | 3.52 | 0.44 | ND | ND | ND | 3 | 1 | 5 | ND | 0.64 | 1363.72 | 46846.74 | 66.89 | 0.98 | 1980.24 | 3.63 | 0.98 | ND | 0.64 | 0.64 | 73.67 | 4.9 | The oil contains an excess of moisture which may be removed by filtration. In other respect, the oil is fit for service. No-fault is | New_Mandala_TRF-2_1.pdf
New Mandala | TR#2 | 11-02-2026 | 04-01-2026 | ETE | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 26 | 46 | L 7.0 | 2 | 3.52 | 0.44 | ND | ND | ND | 3 | 1 | 5 | ND | 0.64 | 1363.72 | 46846.74 | 66.89 | 0.98 | 1980.24 | 3.63 | 0.98 | ND | 0.64 | 0.64 | 73.67 | 4.9 | The oil contains an excess of moisture which may be removed by filtration. In other respect, the oil is fit for service. No-fault is | New_Mandala_TRF-2_1_1.pdf
Nilgiri | TR#1 | 11-02-2026 | 04-01-2026 | British Insulated Calendar Cables | 1000 KVA | 12 KV | Dielectric Fluid-Mineral Base | 54 | 32 | L 7.0 | 5 | 19.32 | 0.76 | ND | ND | ND | 3 | 1 | 5 | ND | 0.31 | 1491.20 | 49727.34 | 52.83 | 1.30 | 1213.32 | 6.50 | 1.30 | ND | 2.70 | 2.70 | 67.14 | 5.2 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Nilgiri_TRF-1_1.pdf
Nilgiri | TR#1 | 11-02-2026 | 04-01-2026 | British Insulated Calendar Cables | 1000 KVA | 12 KV | Dielectric Fluid-Mineral Base | 54 | 32 | L 7.0 | 5 | 19.32 | 0.76 | ND | ND | ND | 3 | 1 | 5 | ND | 0.31 | 1491.20 | 49727.34 | 52.83 | 1.30 | 1213.32 | 6.50 | 1.30 | ND | 2.70 | 2.70 | 67.14 | 5.2 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Nilgiri_TRF-1_1_1.pdf
OLD HDFC | TR#1 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 62 | 20 | L 7.0 | 7 | 89.27 | 4.33 | ND | ND | ND | 3 | 1 | 5 | 1022 | 3.54 | 1528.85 | 49759.37 | 51.79 | 2.55 | 784.42 | 2.50 | 2.55 | ND | ND | ND | 61.42 | 5.2 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Old_Hdfc_TRF-1_1.pdf
OLD HDFC | TR#1 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 62 | 20 | L 7.0 | 7 | 89.27 | 4.33 | ND | ND | ND | 3 | 1 | 5 | 1022 | 3.54 | 1528.85 | 49759.37 | 51.79 | 2.55 | 784.42 | 2.50 | 2.55 | ND | ND | ND | 61.42 | 5.2 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Old_Hdfc_TRF-1_1_1.pdf
PESTOM SAGAR | DT-1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 76 | 7 | L 7.0 | 0 | 297.19 | 25.76 | ND | ND | ND | 3 | 1 | 5 | 962 | 8.84 | 922.52 | 38331.40 | 270.20 | 6.40 | 451.96 | 0.08 | 6.40 | ND | 0.12 | 0.12 | 286.2 | 4.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Pestom_Sagar_DT_1.pdf
PESTOM SAGAR | DT-1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 76 | 7 | L 7.0 | 0 | 297.19 | 25.76 | ND | ND | ND | 3 | 1 | 5 | 962 | 8.84 | 922.52 | 38331.40 | 270.20 | 6.40 | 451.96 | 0.08 | 6.40 | ND | 0.12 | 0.12 | 286.2 | 4.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Pestom_Sagar_DT_1_1.pdf
PESTOM SAGAR | DT-1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 64 | 20 | L 7.0 | 0 | 1056.55 | 70.06 | ND | ND | ND | 3 | 1 | 5 | 972 | 656.80 | 1186.22 | 32718.31 | 274.16 | 62.15 | 1136.75 | 28.73 | 62.15 | 145.31 | 3.73 | 3.73 | 1182.28 | 5.4 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Pestom_Sagar_DT_2.pdf
PESTOM SAGAR | DT-1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 64 | 20 | L 7.0 | 0 | 1056.55 | 70.06 | ND | ND | ND | 3 | 1 | 5 | 972 | 656.80 | 1186.22 | 32718.31 | 274.16 | 62.15 | 1136.75 | 28.73 | 62.15 | 145.31 | 3.73 | 3.73 | 1182.28 | 5.4 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Pestom_Sagar_DT_2_1.pdf
Ragmala | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 1000 KVA | 12 KV | Dielectric Fluid-Mineral Base | 64 | 17 | L 7.0 | 4 | 177.97 | 10.90 | ND | ND | ND | 3 | 1 | 5 | 988 | 0.35 | 1465.50 | 47831.50 | 71.75 | 0.55 | 788.35 | 3.15 | 0.55 | ND | 0.25 | 0.30 | 76.5 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Ragmala_TRF-1_1.pdf
Ragmala | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 1000 KVA | 12 KV | Dielectric Fluid-Mineral Base | 64 | 17 | L 7.0 | 4 | 177.97 | 10.90 | ND | ND | ND | 3 | 1 | 5 | 988 | 0.35 | 1465.50 | 47831.50 | 71.75 | 0.55 | 788.35 | 3.15 | 0.55 | ND | 0.25 | 0.30 | 76.5 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Ragmala_TRF-1_1_1.pdf
SUPREEM | DT-1 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 73 | 17 | L 7.0 | 2 | 768.40 | 51.30 | ND | ND | ND | 3 | 1 | 5 | 1059 | 0.96 | 1092.53 | 45944.35 | 312.67 | 6.72 | 819.22 | 0.62 | 6.72 | ND | 0.53 | 0.53 | 322.7 | 4. | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Suprem_DT-1_1.pdf
SUPREEM | DT-1 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 73 | 17 | L 7.0 | 2 | 768.40 | 51.30 | ND | ND | ND | 3 | 1 | 5 | 1059 | 0.96 | 1092.53 | 45944.35 | 312.67 | 6.72 | 819.22 | 0.62 | 6.72 | ND | 0.53 | 0.53 | 322.7 | 4. | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Suprem_DT-1_1_1.pdf
SUPREEM | DT-1 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 71 | 15 | L 7.0 | 1 | 581.95 | 45.82 | ND | ND | ND | 3 | 1 | 5 | 720 | 2172.17 | 1498.04 | 32513.94 | 123.04 | 162.75 | 604.78 | 145.09 | 162.75 | 358.33 | 10.01 | 10.01 | 2988.94 | 5.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Suprem_DT-1_2.pdf
SUPREEM | DT-1 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 71 | 15 | L 7.0 | 1 | 581.95 | 45.82 | ND | ND | ND | 3 | 1 | 5 | 720 | 2172.17 | 1498.04 | 32513.94 | 123.04 | 162.75 | 604.78 | 145.09 | 162.75 | 358.33 | 10.01 | 10.01 | 2988.94 | 5.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Suprem_DT-1_2_1.pdf
SUPREEM | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 63 | 24 | L 7.0 | 0 | 717.55 | 39.04 | ND | ND | ND | 3 | 1 | 5 | 966 | 0.60 | 1090.06 | 44093.85 | 233.59 | 5.47 | 703.80 | 2.85 | 5.47 | ND | 0.46 | 0.51 | 244.12 | 4.6 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Suprem_DT-2_1.pdf
SUPREEM | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 63 | 24 | L 7.0 | 0 | 717.55 | 39.04 | ND | ND | ND | 3 | 1 | 5 | 966 | 0.60 | 1090.06 | 44093.85 | 233.59 | 5.47 | 703.80 | 2.85 | 5.47 | ND | 0.46 | 0.51 | 244.12 | 4.6 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Suprem_DT-2_1_1.pdf
SUPREEM | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 67 | 19 | L 7.0 | 9 | 694.95 | 28.42 | ND | ND | ND | 3 | 1 | 5 | 994 | 1521.50 | 1265.45 | 32035.08 | 49.14 | 61.70 | 261.09 | 59.04 | 61.70 | 254.61 | 3.02 | 3.02 | 1954.28 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Suprem_DT-2_2.pdf
SUPREEM | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 67 | 19 | L 7.0 | 9 | 694.95 | 28.42 | ND | ND | ND | 3 | 1 | 5 | 994 | 1521.50 | 1265.45 | 32035.08 | 49.14 | 61.70 | 261.09 | 59.04 | 61.70 | 254.61 | 3.02 | 3.02 | 1954.28 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Suprem_DT-2_2_1.pdf
Symphony | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 22 | 55 | L 7.0 | 7 | 4.81 | 0.39 | ND | ND | ND | 3 | 1 | 5 | 147 | 0.26 | 1236.12 | 32131.25 | 69.36 | 0.52 | 876.73 | 0.39 | 0.52 | ND | 0.26 | 0.26 | 71.09 | 4.3 | The oil contains an excess of moisture which may be removed by filtration. In other respect, the oil is fit for service. No-fault is | Symphony_TRF-1_1.pdf
Symphony | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 22 | 55 | L 7.0 | 7 | 4.81 | 0.39 | ND | ND | ND | 3 | 1 | 5 | 147 | 0.26 | 1236.12 | 32131.25 | 69.36 | 0.52 | 876.73 | 0.39 | 0.52 | ND | 0.26 | 0.26 | 71.09 | 4.3 | The oil contains an excess of moisture which may be removed by filtration. In other respect, the oil is fit for service. No-fault is | Symphony_TRF-1_1_1.pdf
Symphony | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 23 | 49 | L 7.0 | 9 | 1.02 | 0.16 | ND | ND | ND | 3 | 1 | 5 | 173 | 0.45 | 1064.03 | 42771.78 | 225.86 | 1.62 | 1069.07 | 1.04 | 1.62 | ND | 0.72 | 0.77 | 230.6 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Symphony_TRF-1_2.pdf
Symphony | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 23 | 49 | L 7.0 | 9 | 1.02 | 0.16 | ND | ND | ND | 3 | 1 | 5 | 173 | 0.45 | 1064.03 | 42771.78 | 225.86 | 1.62 | 1069.07 | 1.04 | 1.62 | ND | 0.72 | 0.77 | 230.6 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Symphony_TRF-1_2_1.pdf
Vensarkar | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 630 KVA | 24 KV | Dielectric Fluid-Mineral Base | 72 | 12 | L 7.0 | 4 | 655.40 | 94.92 | ND | ND | ND | 3 | 1 | 5 | 1271 | 0.33 | 1426.50 | 32242.18 | 48.41 | 1.03 | 544.87 | 0.47 | 1.03 | ND | 0.42 | 0.47 | 51.27 | 4.7 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Vengsarkar_TRF-1_1.pdf
Vensarkar | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 630 KVA | 24 KV | Dielectric Fluid-Mineral Base | 72 | 12 | L 7.0 | 4 | 655.40 | 94.92 | ND | ND | ND | 3 | 1 | 5 | 1271 | 0.33 | 1426.50 | 32242.18 | 48.41 | 1.03 | 544.87 | 0.47 | 1.03 | ND | 0.42 | 0.47 | 51.27 | 4.7 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Vengsarkar_TRF-1_1_1.pdf
Vensarkar | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 630 KVA | 24 KV | Dielectric Fluid-Mineral Base | 70 | 18 | L 7.0 | 3 | 176.84 | 12.66 | ND | ND | ND | 3 | 1 | 5 | 1235 | 1.44 | 1339.43 | 43088.45 | 42.12 | 1.94 | 552.15 | 0.18 | 1.94 | ND | 0.27 | 0.32 | 46.63 | 1.44 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Vengsarkar_TRF-1_2.pdf
Vensarkar | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 630 KVA | 24 KV | Dielectric Fluid-Mineral Base | 70 | 18 | L 7.0 | 3 | 176.84 | 12.66 | ND | ND | ND | 3 | 1 | 5 | 1235 | 1.44 | 1339.43 | 43088.45 | 42.12 | 1.94 | 552.15 | 0.18 | 1.94 | ND | 0.27 | 0.32 | 46.63 | 1.44 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Vengsarkar_TRF-1_2_1.pdf
Vrindavan | TR#1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 65 | 18 | L 7.0 | 1 | 1853.20 | 66.67 | ND | ND | ND | 3 | 1 | 5 | 1019 | 0.31 | 1271.38 | 42194.20 | 86.15 | 1.28 | 462.35 | 0.35 | 1.28 | ND | ND | ND | 88.27 | 4.4 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Vrindavan_DT-1_1.pdf
Vrindavan | TR#1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 65 | 18 | L 7.0 | 1 | 1853.20 | 66.67 | ND | ND | ND | 3 | 1 | 5 | 1019 | 0.31 | 1271.38 | 42194.20 | 86.15 | 1.28 | 462.35 | 0.35 | 1.28 | ND | ND | ND | 88.27 | 4.4 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Vrindavan_DT-1_1_1.pdf
Vrindavan | TR#1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 61 | 21 | L 7.0 | 1 | 1740.20 | 86.45 | ND | ND | ND | 3 | 1 | 5 | 1039 | 486.92 | 1237.09 | 32864 | 25.60 | 19.82 | 180.52 | 35.69 | 19.82 | 264.60 | 0.81 | 0.86 | 835.33 | 5.4 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Vrindavan_DT-1_2.pdf
Vrindavan | TR#1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 61 | 21 | L 7.0 | 1 | 1740.20 | 86.45 | ND | ND | ND | 3 | 1 | 5 | 1039 | 486.92 | 1237.09 | 32864 | 25.60 | 19.82 | 180.52 | 35.69 | 19.82 | 264.60 | 0.81 | 0.86 | 835.33 | 5.4 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Vrindavan_DT-1_2_1.pdf
Vrindavan | TR#2 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 62 | 19 | L 7.0 | 1 | 175.71 | 10.90 | ND | ND | ND | 3 | 1 | 5 | 1205 | 1325.31 | 1343.45 | 43959.34 | 116.94 | 136.72 | 941.18 | 150.40 | 136.72 | 546.66 | 6.91 | 6.91 | 2293.66 | 4.7 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Vrindavan_DT-2_1.pdf
Vrindavan | TR#2 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 62 | 19 | L 7.0 | 1 | 175.71 | 10.90 | ND | ND | ND | 3 | 1 | 5 | 1205 | 1325.31 | 1343.45 | 43959.34 | 116.94 | 136.72 | 941.18 | 150.40 | 136.72 | 546.66 | 6.91 | 6.91 | 2293.66 | 4.7 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Vrindavan_DT-2_1_1.pdf
Vrindavan | TR#2 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 29 | 57 | L 7.0 | 1 | 186.45 | 23.00 | ND | ND | ND | 3 | 1 | 5 | 1073 | 1.28 | 840.05 | 42010.54 | 541.99 | 6.34 | 3083.90 | 3.08 | 6.34 | ND | 0.09 | 0.13 | 553.79 | 4.4 | The oil contains an excess of moisture which may be removed by filtration. In other respect, the oil is fit for service. No-fault is | Vrindavan_DT-2_2.pdf
Vrindavan | TR#2 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 29 | 57 | L 7.0 | 1 | 186.45 | 23.00 | ND | ND | ND | 3 | 1 | 5 | 1073 | 1.28 | 840.05 | 42010.54 | 541.99 | 6.34 | 3083.90 | 3.08 | 6.34 | ND | 0.09 | 0.13 | 553.79 | 4.4 | The oil contains an excess of moisture which may be removed by filtration. In other respect, the oil is fit for service. No-fault is | Vrindavan_DT-2_2_1.pdf
Sector 1 western S/s / BARC TR#1 |  | 11-02-2026 | 04-01-2026 | Bharat Bijlee Limited | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 71 | 17 | L 7.0 | 7 | 166.67 | 10.40 | ND | ND | ND | 3 | 1 | 5 | 1250 | 2.65 | 1198.01 | 32212.60 | 91.01 | 1.01 | 890.36 | 0.25 | 1.01 | ND | 0.13 | 0.17 | 95.3 | 4.2 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Western_Sector_TRF-1_1.pdf
Sector 1 western S/s / BARC TR#1 |  | 11-02-2026 | 04-01-2026 | Bharat Bijlee Limited | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 71 | 17 | L 7.0 | 7 | 166.67 | 10.40 | ND | ND | ND | 3 | 1 | 5 | 1250 | 2.65 | 1198.01 | 32212.60 | 91.01 | 1.01 | 890.36 | 0.25 | 1.01 | ND | 0.13 | 0.17 | 95.3 | 4.2 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Western_Sector_TRF-1_1_1.pdf
Sector 2 western S/s / BARC TR#2 |  | 11-02-2026 | 04-01-2026 | Bharat Bijlee Limited | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 59 | 24 | L 7.0 | 8 | 8.08 | 0.93 | ND | ND | ND | 3 | 1 | 5 | 958 | 1.47 | 1344.99 | 44003.28 | 106.26 | 1.24 | 1029.30 | 1.75 | 1.24 | ND | 0.32 | 0.37 | 111.55 | 4.6 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Western_Sector_TRF-2_1.pdf
Sector 2 western S/s / BARC TR#2 |  | 11-02-2026 | 04-01-2026 | Bharat Bijlee Limited | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 59 | 24 | L 7.0 | 8 | 8.08 | 0.93 | ND | ND | ND | 3 | 1 | 5 | 958 | 1.47 | 1344.99 | 44003.28 | 106.26 | 1.24 | 1029.30 | 1.75 | 1.24 | ND | 0.32 | 0.37 | 111.55 | 4.6 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Western_Sector_TRF-2_1_1.pdf
4D / BARC-TR#1 |  | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 60 | 20 | L 7.0 | 9 | 745.80 | 98.88 | ND | ND | ND | 3 | 1 | 5 | 1148 | 0.30 | 1548.00 | 47869.85 | 22.15 | 0.65 | 486.75 | 0.40 | 0.65 | ND | 0.15 | 0.20 | 23.95 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | 4 D css BARC TR-1.pdf
Aacharya Udyog | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 63 | 23 | L 7.0 | 1 | 189.28 | 14.07 | ND | ND | ND | 3 | 1 | 5 | 1079 | 10.08 | 1287.54 | 43083.00 | 74.61 | 1.53 | 802.58 | 1.35 | 1.53 | ND | 0.14 | 0.14 | 87.99 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | AACHARYA UDYOG CSS. TR-1.pdf
Aacharya Udyog | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 73 | 14 | L 7.0 | 0 | 99.44 | 8.31 | ND | ND | ND | 3 | 1 | 5 | 945 | 0.38 | 1627.78 | 51749.39 | 29.59 | 0.97 | 645.08 | 0.38 | 0.97 | ND | 0.32 | 0.32 | 32.12 | 5.4 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | ACHARYA UDYOG CSS TR-1.pdf
Address- | DT-2 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 65 | 22 | L 7.0 | 3 | 717.55 | 102.83 | ND | ND | ND | 3 | 1 | 5 | 1060 | 934.25 | 1294.07 | 32048.58 | 60.98 | 66.60 | 310.10 | 61.26 | 66.60 | 260.33 | 3.02 | 3.02 | 1391.8 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | address dss dt-2.pdf
Akash Ganga | TR#1 | 21-02-2026 | 04-01-2026 | ETE | 1000 KVA | 12 KV | Dielectric Fluid-Mineral Base | 24 | 85 | L 7.0 | 1 | 1.71 | 0.28 | ND | ND | ND | 3 | 1 | 5 | 45 | 12.52 | 999.60 | 40253.05 | 187.11 | 1.60 | 1709.06 | 2.31 | 1.60 | ND | 0.84 | 0.84 | 205.6 | 4.2 | The oil is heavily contaminated with acidic impurities and is UNFIT for retention in the transformer. The resistivity value is below the | Akash Ganga CSS TRF-1.pdf
GLENDER CROFT | TR-1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 78 | 18 | L 7.0 | 6 | 159.33 | 10.90 | ND | ND | ND | 3 | 1 | 5 | 715 | 1.65 | 1513.00 | 32356.65 | 90.80 | 0.70 | 1103.60 | 1.85 | 0.70 | ND | 0.40 | 0.40 | 95.95 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | glen croft css TR-1.pdf
GLENDER CROFT | TR-1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 59 | 22 | L 7.0 | 7 | 296.62 | 21.02 | ND | ND | ND | 3 | 1 | 5 | 1042 | 6.20 | 1140.66 | 32150.37 | 118.49 | 4.09 | 587.27 | 4.75 | 4.09 | 5.28 | 0.26 | 0.26 | 139.59 | 4.4 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Glen croft CSS TR-1.pdf
GODREJ DSS | DT-1 | 22-02-2026 | 04-01-2026 | Godrej Industries Limited |  | 12 KV | Dielectric Fluid-Mineral Base | 75 | 15 | L 7.0 | 6 | 104.53 | 6.05 | ND | ND | ND | 3 | 1 | 5 | 888 | 0.38 | 1430.02 | 45859.20 | 25.20 | 1.73 | 401.71 | 3.07 | 1.73 | 9.79 | 0.14 | 0.19 | 40.64 | 4.8 | The oil is fit for use in the equipment, and no corrective action is required at this time. No fault is detected from the gas analysis; | GODREJ DSS DT-1.pdf
GODREJ DSS | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 12 KV | Dielectric Fluid-Mineral Base | 63 | 17 | L 7.0 | 9 | 179.67 | 12.20 | ND | ND | ND | 3 | 1 | 5 | 1077 | 54.00 | 1186.17 | 39231.92 | 16.24 | 4.63 | 509.88 | 5.21 | 4.63 | 48.30 | 0.37 | 0.41 | 129.61 | 4.1 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Godrej dss dt -2.pdf
GODREJ DSS | DT-1 | 11-02-2026 | 04-01-2026 | Godrej Industries Limited |  | 12 KV | Dielectric Fluid-Mineral Base | 73 | 17 | L 7.0 | 5 | 222.05 | 26.33 | ND | ND | ND | 3 | 1 | 5 | 921 | 306.72 | 1272.93 | 31985.48 | 31.18 | 21.41 | 352.99 | 17.72 | 21.41 | 112.70 | 0.95 | 0.95 | 492.32 | 4.3 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Godrej dss dt-1.pdf
GODREJ DSS | DT-2 | 21-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 12 KV | Dielectric Fluid-Mineral Base | 76 | 14 | L 7.0 | 8 | 988.75 | 98.25 | ND | ND | ND | 3 | 1 | 5 | 967 | 0.30 | 1477.35 | 47725.95 | 30.80 | 1.15 | 431.35 | 1.85 | 1.15 | 1.65 | 0.15 | 0.20 | 36.2 | 5.0 | The oil is fit for use in the equipment, and no corrective action is required at this time. No fault is detected from the gas analysis; | Godrej dss DT-2.pdf
GODREJ STP | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 630 KVA | 24 KV | Dielectric Fluid-Mineral Base | 76 | 12 | L 7.0 | 1 | 180.24 | 15.93 | ND | ND | ND | 3 | 1 | 5 | 1061 | 0.35 | 1524.45 | 32358.75 | 49.00 | 1.40 | 593.85 | 0.55 | 1.40 | ND | 0.50 | 0.55 | 52.5 | 5.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | GODREJ STP CSS TR-1.pdf
GODREJ STP | TR#1 | 11-02-2026 | 04-01-2026 | CG Power and Industrial Solution Limited | 630 KVA | 24 KV | Dielectric Fluid-Mineral Base | 65 | 16 | L 7.0 | 1 | 206.23 | 17.91 | ND | ND | ND | 3 | 1 | 5 | 1019 | 0.55 | 1490.30 | 47844.05 | 45.25 | 2.85 | 596.15 | 0.15 | 2.85 | 0.25 | 0.10 | 0.10 | 49.45 | 5.0 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | GODREJ STP TR-1.pdf
OLD HDFC | TR#1 | 21-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 56 | 22 | L 7.0 | 8 | 1768.45 | 94.36 | ND | ND | ND | 3 | 1 | 5 | 1026 | 0.14 | 1752.66 | 42864.89 | 30.51 | 0.32 | 375.71 | 0.86 | 0.32 | ND | 0.05 | 0.05 | 31.93 | 4.5 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | HDFC OLD CSS TR-1.pdf
Hiranandani DSS | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 62 | 19 | L 7.0 | 5 | 10.28 | 1.38 | ND | ND | ND | 3 | 1 | 5 | 940 | 1438.26 | 605.62 | 35257.93 | 191.55 | 103.19 | 655.86 | 100.38 | 103.19 | 554.08 | 2.55 | 2.55 | 2396.37 | 3.7 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Hiranandani dss dt -1.pdf
Hiranandani DSS | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 71 | 15 | L 7.0 | 3 | 153.68 | 33.56 | ND | ND | ND | 3 | 1 | 5 | 1017 | 1.92 | 613.93 | 25783.73 | 228.74 | 1.62 | 994.98 | 1.05 | 1.62 | ND | 0.05 | 0.05 | 233.59 | 2.7 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Hiranandani dss dt-1.pdf
Hiranandani DSS | DT#2 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 75 | 13 | L 7.0 | 0 | 166.67 | 17.18 | ND | ND | ND | 3 | 1 | 5 | 1026 | 0.40 | 950.76 | 38045.00 | 254.32 | 2.24 | 1217.72 | 3.08 | 2.24 | ND | 0.04 | 0.08 | 260.28 | 4.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | hiranandani dss dt-2.pdf
Hiranandani DSS | DT#2 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 64 | 16 | L 7.0 | 5 | 197.75 | 24.63 | ND | ND | ND | 3 | 1 | 5 | 986 | 205.15 | 620.48 | 23788.68 | 3.98 | 8.53 | 68.78 | 6.53 | 8.53 | 59.23 | 0.28 | 0.30 | 284.2 | 2.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Hiranandani dss. dt-2.pdf
klick nixion | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 75 | 16 | L 7.0 | 3 | 128.26 | 16.27 | ND | ND | ND | 3 | 1 | 5 | 914 | 0.63 | 1008.68 | 43151.18 | 181.98 | 14.36 | 489.51 | 9.00 | 14.36 | ND | 3.83 | 3.83 | 225.38 | 4.5 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Killick nixon DSS Dt-1.pdf
klick nixion | DT#1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 64 | 16 | L 7.0 | 3 | 402.85 | 16.27 | ND | ND | ND | 3 | 1 | 5 | 868 | 1572.00 | 1248.49 | 32099.16 | 142.05 | 144.35 | 285.89 | 130.73 | 144.35 | 312.66 | 8.60 | 8.60 | 2327.04 | 4.6 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Killick nixon DSS- dt1.pdf
L&T | DT#2 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | L& T DT-2.pdf
L & T | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | L&T dss Dt-1.pdf
L & T | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | L&T dt 1.pdf
L & T | DT-1 | 11-02-2026 | 04-01-2026 | Schneider Electric Infrastructure Ltd | 20000 KVA | 36 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | L&T Dt-1.pdf
MARKET CITY | DT-1 | 11-02-2026 | 04-01-2026 | ABB |  | 36 KV | Dielectric Fluid-Mineral Base | 65 | 20 | L 7.0 | 9 | 100.01 | 10.72 | ND | ND | ND | 3 | 1 | 5 | 1067 | 1447.88 | 1352.98 | 31970.32 | 168.05 | 89.89 | 388.22 | 96.34 | 89.89 | 263.74 | 12.85 | 12.85 | 2129.94 | 3.6 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Market city dss dt-1.pdf
MARKET CITY | DT-2 | 22-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 36 KV | Dielectric Fluid-Mineral Base | 63 | 23 | L 7.0 | 0 | 361.04 | 16.95 | ND | ND | ND | 3 | 1 | 5 | 1002 | 0.26 | 1212.86 | 41025.31 | 41.80 | 2.41 | 651.19 | 1.03 | 2.41 | ND | 0.17 | 0.17 | 45.93 | 4.3 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Market city css DT-2.pdf
MARKET CITY | DT-1 | 11-02-2026 | 04-01-2026 | ABB |  | 36 KV | Dielectric Fluid-Mineral Base | 63 | 21 | L 7.0 | 0 | 762.75 | 197.75 | ND | ND | ND | 3 | 1 | 5 | 1122 | 1.02 | 679.11 | 32637.65 | 173.64 | 3.39 | 311.43 | 0.84 | 3.39 | ND | 0.12 | 0.15 | 179.94 | 3.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Market city css dt1.pdf
MARKET CITY | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. |  | 36 KV | Dielectric Fluid-Mineral Base | 75 | 16 | L 7.0 | 9 | 46.44 | 2.94 | ND | ND | ND | 3 | 1 | 5 | 959 | 992.52 | 1284.57 | 32113.11 | 38.84 | 64.49 | 236.75 | 62.24 | 64.49 | 275.81 | 4.32 | 4.32 | 1445.69 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | market city dss dt-2.pdf
MARWAHA IND | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | 4.24 | 350.80 | 38293.72 | 89.48 | 3.64 | 782.24 | 4.48 | 3.64 | ND | 1.52 | 1.52 | 171.4 | 4.0 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | MARWAHA CSS TR -1.pdf
MARWAHA IND | TR#1 | 11-02-2026 | 04-01-2026 | EMCO | 1250 KVA | 24 KV | Natural Esters | ND | ND | L 1.5 | ND | ND | ND | ND | ND | ND | 5 | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | ND | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | MARWAHA IND CSS TR 1.pdf
New Mandala | TR#1 | 21-02-2026 | 04-01-2026 | ETE | 1250 KVA | 12 KV | Dielectric Fluid-Mineral Base | 26 | 73 | L 7.0 | 1 | 0.63 | 0.11 | ND | ND | ND | 3 | 1 | 5 | 52 | 31.64 | 929.79 | 43164.27 | 206.37 | 4.37 | 3328.83 | 19.49 | 4.37 | ND | 2.39 | 2.43 | 267.64 | 4.5 | The oil is heavily contaminated with acidic impurities and is UNFIT for retention in the transformer. The resistivity value is below the | New Mandala TR#1.pdf
OLD HDFC | TR#1 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 1250 KVA | 24 KV | Dielectric Fluid-Mineral Base | 62 | 20 | L 7.0 | 7 | 89.27 | 4.33 | ND | ND | ND | 3 | 1 | 5 | 1022 | 3.54 | 1528.85 | 49759.37 | 51.79 | 2.55 | 784.42 | 2.50 | 2.55 | ND | ND | ND | 61.42 | 5.2 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | OLD HDFC CSS.pdf
PESTOM SAGAR | DT-1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 64 | 20 | L 7.0 | 0 | 1056.55 | 70.06 | ND | ND | ND | 3 | 1 | 5 | 972 | 656.80 | 1186.22 | 32718.31 | 274.16 | 62.15 | 1136.75 | 28.73 | 62.15 | 145.31 | 3.73 | 3.73 | 1182.28 | 5.4 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Pestom sagar dss DT-1.pdf
PESTOM SAGAR | DT-1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 76 | 7 | L 7.0 | 0 | 297.19 | 25.76 | ND | ND | ND | 3 | 1 | 5 | 962 | 8.84 | 922.52 | 38331.40 | 270.20 | 6.40 | 451.96 | 0.08 | 6.40 | ND | 0.12 | 0.12 | 286.2 | 4.0 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Pestom sagar dt-1.pdf
SUPREEM | DT-2 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 67 | 19 | L 7.0 | 9 | 694.95 | 28.42 | ND | ND | ND | 3 | 1 | 5 | 994 | 1521.50 | 1265.45 | 32035.08 | 49.14 | 61.70 | 261.09 | 59.04 | 61.70 | 254.61 | 3.02 | 3.02 | 1954.28 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Supreme DSS DT-2.pdf
SUPREEM | DT-1 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 73 | 17 | L 7.0 | 2 | 768.40 | 51.30 | ND | ND | ND | 3 | 1 | 5 | 1059 | 0.96 | 1092.53 | 45944.35 | 312.67 | 6.72 | 819.22 | 0.62 | 6.72 | ND | 0.53 | 0.53 | 322.7 | 4. | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | Supreme DSS DT-1.pdf
SUPREEM | DT-1 | 11-02-2026 | 04-01-2026 | Kirloskar Electric Company Ltd. | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 71 | 15 | L 7.0 | 1 | 581.95 | 45.82 | ND | ND | ND | 3 | 1 | 5 | 720 | 2172.17 | 1498.04 | 32513.94 | 123.04 | 162.75 | 604.78 | 145.09 | 162.75 | 358.33 | 10.01 | 10.01 | 2988.94 | 5.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Supreme DT-1.pdf
Vrindavan | TR#2 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 62 | 19 | L 7.0 | 1 | 175.71 | 10.90 | ND | ND | ND | 3 | 1 | 5 | 1205 | 1325.31 | 1343.45 | 43959.34 | 116.94 | 136.72 | 941.18 | 150.40 | 136.72 | 546.66 | 6.91 | 6.91 | 2293.66 | 4.7 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | Vrindavan dss dt2.pdf
Vrindavan | TR#1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 61 | 21 | L 7.0 | 1 | 1740.20 | 86.45 | ND | ND | ND | 3 | 1 | 5 | 1039 | 486.92 | 1237.09 | 32864 | 25.60 | 19.82 | 180.52 | 35.69 | 19.82 | 264.60 | 0.81 | 0.86 | 835.33 | 5.4 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | VRINDAVAN DT.1.pdf
Vrindavan | TR#2 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 29 | 57 | L 7.0 | 1 | 186.45 | 23.00 | ND | ND | ND | 3 | 1 | 5 | 1073 | 1.28 | 840.05 | 42010.54 | 541.99 | 6.34 | 3083.90 | 3.08 | 6.34 | ND | 0.09 | 0.13 | 553.79 | 4.4 | The oil contains an excess of moisture which may be removed by filtration. In other respect, the oil is fit for service. No-fault is | VRINDAVAN DT.2.pdf
Vrindavan | TR#1 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 65 | 18 | L 7.0 | 1 | 1853.20 | 66.67 | ND | ND | ND | 3 | 1 | 5 | 1019 | 0.31 | 1271.38 | 42194.20 | 86.15 | 1.28 | 462.35 | 0.35 | 1.28 | ND | ND | ND | 88.27 | 4.4 | Oil is Fit to be used in equipment. No Action for Correction is needed at the moment. No-fault is detectable from the gas analysis. | VRINDAVAN DT1.pdf

## Sheet1
BDV (KV) | Water Content (ppm)
80 | 4
81 | 4
78 | 5
78 | 6
77 | 6
77 | 6
72 | 7
74 | 7
74 | 7
76 | 7
76 | 7
76 | 7
73 | 8
73 | 8
73 | 8
73 | 8
70 | 10
70 | 10
70 | 10
70 | 10
69 | 11
69 | 11
69 | 11
68 | 12
68 | 12
76 | 12
76 | 12
72 | 12
72 | 12
76 | 12
67 | 13
68 | 13
67 | 13
75 | 13
75 | 13
75 | 13
73 | 14
73 | 14
76 | 14
76 | 14
73 | 14
76 | 14
65 | 15
65 | 15
73 | 15
73 | 15
75 | 15
75 | 15
71 | 15
71 | 15
71 | 15
71 | 15
75 | 15
71 | 15
71 | 15
64 | 16
62 | 16
62 | 16
65 | 16
65 | 16
64 | 16
64 | 16
64 | 16
64 | 16
75 | 16
75 | 16
75 | 16
75 | 16
65 | 16
64 | 16
75 | 16
64 | 16
75 | 16
60 | 17
60 | 17
73 | 17
73 | 17
63 | 17
63 | 17
64 | 17
64 | 17
73 | 17
73 | 17
71 | 17
71 | 17
63 | 17
73 | 17
73 | 17
62 | 18
62 | 18
62 | 18
65 | 18
65 | 18
78 | 18
78 | 18
70 | 18
70 | 18
65 | 18
65 | 18
78 | 18
65 | 18
61 | 19
62 | 19
62 | 19
67 | 19
67 | 19
62 | 19
62 | 19
62 | 19
67 | 19
62 | 19
66 | 20
66 | 20
64 | 20
64 | 20
65 | 20
65 | 20
62 | 20
62 | 20
64 | 20
64 | 20
60 | 20
65 | 20
62 | 20
64 | 20
66 | 21
66 | 21
63 | 21
63 | 21
61 | 21
61 | 21
63 | 21
61 | 21
58 | 22
65 | 22
65 | 22
59 | 22
59 | 22
65 | 22
59 | 22
56 | 22
61 | 23
57 | 23
63 | 23
63 | 23
63 | 23
63 | 23
63 | 23
63 | 23
64 | 24
64 | 24
63 | 24
63 | 24
59 | 24
59 | 24
55 | 25
55 | 25
52 | 28
52 | 28
52 | 28
51 | 29
51 | 29
52 | 29
52 | 29
54 | 32
54 | 32
56 | 36
56 | 36
28 | 46
28 | 46
26 | 46
26 | 46
23 | 49
23 | 49
22 | 55
22 | 55
29 | 57
29 | 57
29 | 57
26 | 73
26 | 73
26 | 73
24 | 85
24 | 85
24 | 85
24 | 85
24 | 85
Address- | DT-2 | 11-02-2026 | 04-01-2026 | ABB | 20000 KVA | 36 KV | Dielectric Fluid-Mineral Base | 65 | 22 | L 7.0 | 3 | 717.55 | 102.83 | ND | ND | ND | 3 | 1 | 5 | 1060 | 934.25 | 1294.07 | 32048.58 | 60.98 | 66.60 | 310.10 | 61.26 | 66.60 | 260.33 | 3.02 | 3.02 | 1391.8 | 4.5 | The oil is fit for service. Gas Results indicate no overheating. Continue normal operation of the transformer and monitor regularly for any | address dss dt-2.pdf