## DGA Data
Dissolved Gas Analysis (DGA) Report — Transformer Oil Test
Gas | Symbol | Unit | Measured Value (ppm) | Limit (ppm) | Status
Total Gas Content (TGC) | TGC | % v/v | 5 | NS | Not Specified
Hydrogen | H₂ | ppm | 0.3 | 50 Max | Acceptable
Oxygen | O₂ | ppm | 1548 | NS | Not Specified
Nitrogen | N₂ | ppm | 47869.85 | NS | Not Specified
Carbon Monoxide | CO | ppm | 22.15 | 400 Max | Acceptable
Methane | CH₄ | ppm | 0.65 | 30 Max | Acceptable
Carbon Dioxide | CO₂ | ppm | 486.75 | 3800 Max | Acceptable
Ethylene | C₂H₄ | ppm | 0.4 | 60 Max | Acceptable
Ethane | C₂H₆ | ppm | 0.1 | 20 Max | Acceptable
Acetylene | C₂H₂ | ppm | 0 | 2 Max | Acceptable
Propylene | C₃H₆ | ppm | 0.15 | NS | Not Specified
Propane | C₃H₈ | ppm | 0.2 | NS | Not Specified
Total Dissolved Combustible Gas | TDCG | mg/kg | 23.95 | NS | Not Specified
TDCG/TGC | Ratio | % | 0.048 | 8% max | Acceptable
Duval's Triangle Key Gases (CH₄, C₂H₄, C₂H₂)
Parameter | Gas | Value (ppm) | % of Sum | Duval X-coord Input | Duval Y-coord Input
Methane | CH₄ |  |  | N/A | N/A
Ethylene | C₂H₄ |  |  |  | N/A
Acetylene | C₂H₂ |  |  | N/A
Sum
Duval Fault Zone: D2 — High Energy Electrical Discharge (Arc)

## Duval Triangle
Duval's Triangle — IEC 60599 Fault Zone Analysis
Gas | Value (ppm) | % Contribution
Methane (CH₄) | 1.15 | 24.73%
Ethylene (C₂H₄) | 1.85 | 39.78%
Acetylene (C₂H₂) | 1.65 | 35.48%
Total | 4.65 | 100.00%
Duval Zone | D2 | High Energy Electrical Discharge (Arc)