## 1_Gas Data
DGA REPORT — Full Gas Concentration Data (IS 9434 / IEEE C57.104)
Parameter | Symbol | Unit | Measured Value | Limit | Status | Remark
Total Gas Content | TGC | % v/v | 5 | NS | Not Specified
Hydrogen | H₂ | ppm | 0.3 | 50 Max | Acceptable | Key fault gas
Oxygen | O₂ | ppm | 1477.35 | NS | Not Specified | Monitor O2/N2 ratio
Nitrogen | N₂ | ppm | 47725.95 | NS | Not Specified
Carbon Monoxide | CO | ppm | 30.8 | 400 Max | Acceptable | Paper degradation indicator
Methane | CH₄ | ppm | 1.15 | 30 Max | Acceptable | Key fault gas
Carbon Dioxide | CO₂ | ppm | 431.35 | 3800 Max | Acceptable | Paper degradation indicator
Ethylene | C₂H₄ | ppm | 1.85 | 60 Max | Acceptable | Key fault gas
Ethane | C₂H₆ | ppm | 0.1 | 20 Max | Acceptable | Key fault gas
Acetylene | C₂H₂ | ppm | 1.65 | 2 Max | Acceptable | Key fault gas — arcing
Propylene | C₃H₆ | ppm | 0.15 | NS | Not Specified
Propane | C₃H₈ | ppm | 0.2 | NS | Not Specified
Total Dissolved Comb Gas | TDCG | ppm | 35.85 | 720 Max | Acceptable | IEEE Level 1 threshold
CO₂/CO Ratio | CO₂/CO | — | 14.005 | 3–10 Normal | Not Specified | Cellulose degradation
O₂/N₂ Ratio | O₂/N₂ | — | 0.031 | > 0.3 Normal | Not Specified | Breathing indicator

## 2_Duval Triangle
DUVAL'S TRIANGLE — IEC 60599 Fault Zone Analysis
Gas | Value (ppm) | % of Sum
Methane CH₄ | 1.150 | 24.73%
Ethylene C₂H₄ | 1.850 | 39.78%
Acetylene C₂H₂ | 1.650 | 35.48%
Total | 4.650 | 100.00%
Fault Zone | D2 | High Energy Discharge (Arc)

## 3_Ratio Methods
RATIO METHODS — Rogers / Doernenburg / IEC 60599
ROGERS RATIO METHOD (IEC 60599)
Ratio | Value | Meaning | Code Range
C₂H₂/C₂H₄ | 0.8919 | Discharge indicator | 0.1–3.0
CH₄/H₂ | 3.8333 | Thermal vs PD | 0.1–1.0
C₂H₄/C₂H₆ | 18.5 | Thermal level | 1.0–3.0
Rogers Diagnosis: Unclassified (codes: C2H2/C2H4=1, CH4/H2=2, C2H4/C2H6=2)
DOERNENBURG RATIO METHOD
Ratio | Value | Threshold | Valid?
CH₄/H₂ | 3.8333 | > 1.0 | No (insufficient gas levels)
C₂H₂/C₂H₄ | 0.8919 | ≥ 0.75 | No (insufficient gas levels)
C₂H₂/CH₄ | 1.4348 | ≥ 0.3 | No (insufficient gas levels)
Doernenburg Diagnosis: Insufficient gas levels — Doernenburg method not applicable
IEC 60599 REVISED RATIO METHOD
Ratio | Value | Zone
C₂H₂/C₂H₄ | 0.8919 | < 0.1 ¦ 0.1–3 ¦ > 3
CH₄/H₂ | 3.8333 | < 0.1 ¦ 0.1–1 ¦ > 1
IEC 60599 Diagnosis: Discharge of High Energy (arcing)

## 4_KeyGas_TDCG
KEY GAS METHOD & TDCG ASSESSMENT (IEEE C57.104)
KEY GAS METHOD (IEEE C57.104 / Transformer Guide)
Gas | Value (ppm) | Fault Indication | Dominant?
H₂ | 0.3 | Corona / Partial Discharge | —
CH₄ | 1.15 | Low-temp thermal (< 300°C) | —
C₂H₄ | 1.85 | High-temp thermal in oil (> 300°C) | —
C₂H₂ | 1.65 | Electrical arcing | —
C₂H₆ | 0.1 | Low-moderate thermal (< 200°C) | —
CO | 30.8 | Paper/cellulose overheating | ★ YES
Key Gas Diagnosis: CO dominant → Thermal fault involving cellulose (paper/pressboard overheating)
TDCG ASSESSMENT — IEEE C57.104
Level | TDCG Range (ppm) | Condition | Recommended Action
Level 1 | ≤ 720 | Normal | No action required
Level 2 | 721 – 1920 | Caution | Resample in 1 month
Level 3 | 1921 – 4630 | Warning | Resample in 1 week; plan inspection
Level 4 | > 4630 | Critical | Immediate action / consider taking offline
TDCG = 35.85 ppm → Level 1: Normal Operation ¦ Action: No action required.
CO₂/CO RATIO — Cellulose / Paper Insulation Assessment
CO₂ | 431.35
CO | 30.8
CO₂/CO Ratio | 14.005
Interpretation: Possible CO₂ from non-fault source OR extensive paper degradation

## 5_Summary
DGA ANALYSIS — CONSOLIDATED SUMMARY
Method | Result | Severity | Remarks
Duval Triangle | D2 — High Energy Discharge (Arc) | Critical | IEC 60599
Rogers Ratio | Unclassified (codes: C2H2/C2H4=1, CH4/H2=2, C2H4/C2H6=2) | Normal | IEC 60599
Doernenburg | Insufficient gas levels — Doernenburg method not applicable | Normal | Min gas threshold may not be met
IEC 60599 Revised | Discharge of High Energy (arcing) | Moderate | IEC 60599
Key Gas | CO dominant — Thermal fault involving cellulose (paper/pressboard overheating) | Low | IEEE C57.104
TDCG | Level 1: Normal Operation (35.85 ppm) | Normal | IEEE C57.104
CO₂/CO Ratio | Possible CO₂ from non-fault source OR extensive paper degradation | Normal | Ratio = 14.00
OVERALL ASSESSMENT: CRITICAL (Severity Index = 0.85)